{"text_format":"3","workbook":"xlsx","n_sheets":2,"sheets":["04）调节阀","05）切断阀"],"not_rendered":{"images":2,"defined_names":3,"comments":2},"read":"whole","date_system":"1900"}

{"sheet":"04）调节阀","index":0,"n_rows":154,"n_cols":15,"rows_kept":154,"merged":[[0,8,0,17],[1,0,1,1],[1,2,1,4],[1,5,1,7],[1,8,1,12],[1,14,1,16],[2,0,2,1],[2,2,2,4],[2,5,2,7],[2,8,2,9],[2,11,2,12],[2,14,2,16],[3,0,3,1],[3,2,3,4],[3,5,3,7],[3,8,3,9],[3,11,3,12],[3,14,3,16],[4,1,5,6],[4,7,5,9],[4,10,4,13],[4,14,4,17],[5,10,5,13],[5,14,5,17],[6,1,6,6],[6,7,6,9],[6,10,6,13],[6,14,6,17],[7,1,8,6],[7,7,8,9],[7,10,7,13],[7,14,7,17],[8,10,8,13],[8,14,8,17],[9,1,10,6],[9,7,10,9],[9,10,9,13],[9,14,9,17],[10,10,10,13],[10,14,10,17],[11,1,12,6],[11,7,12,9],[11,10,11,17],[12,10,12,13],[12,14,12,17],[13,1,13,2],[13,3,13,6],[13,7,14,9],[13,10,13,13],[13,14,13,17],[14,1,14,2],[14,3,14,6],[14,10,14,13],[14,14,14,17],[15,1,15,2],[15,4,15,6],[15,7,16,9],[15,10,15,13],[15,14,15,17],[16,1,16,2],[16,4,16,6],[16,10,16,13],[16,14,16,17],[17,1,17,2],[17,4,17,6],[17,7,18,9],[17,10,17,13],[17,14,17,17],[18,1,18,2],[18,4,18,6],[18,10,18,13],[18,14,18,17],[19,1,19,2],[19,4,19,6],[19,7,20,9],[19,10,19,13],[19,14,19,17],[20,1,20,2],[20,4,20,6],[20,10,20,13],[20,14,20,17],[21,1,21,2],[21,4,21,6],[21,7,21,9],[21,10,21,17],[22,1,22,2],[22,4,22,6],[22,7,22,9],[22,10,22,13],[22,14,22,17],[23,1,23,2],[23,4,23,6],[23,7,23,9],[23,10,23,13],[23,14,23,17],[24,1,24,2],[24,4,24,6],[24,7,24,9],[24,10,24,13],[24,14,24,17],[25,1,25,2],[25,4,25,6],[25,7,25,9],[25,10,25,13],[25,14,25,17],[26,1,26,2],[26,4,26,6],[26,7,26,9],[26,10,26,13],[26,14,26,17],[27,1,27,2],[27,4,27,6],[27,7,27,9],[27,10,27,13],[27,14,27,17],[28,1,28,2],[28,4,28,6],[28,7,28,9],[28,10,28,13],[28,14,28,17],[29,1,29,2],[29,3,29,6],[29,7,29,9],[29,10,29,13],[29,14,29,17],[30,1,30,2],[30,3,30,6],[30,7,30,9],[30,10,30,13],[30,14,30,17],[31,1,31,2],[31,3,31,6],[31,7,31,9],[31,10,31,13],[31,14,31,17],[32,1,32,2],[32,3,32,6],[32,7,32,9],[32,10,32,17],[33,1,33,2],[33,3,33,6],[33,7,33,9],[33,10,33,13],[33,14,33,17],[34,1,34,2],[34,3,34,6],[34,7,34,9],[34,10,34,13],[34,14,34,17],[35,1,35,2],[35,3,35,6],[35,7,35,9],[35,10,35,13],[35,14,35,17],[36,1,36,2],[36,3,36,6],[36,7,36,9],[36,10,36,13],[36,14,36,17],[37,1,37,2],[37,3,37,6],[37,7,37,9],[37,10,37,13],[37,14,37,17],[38,1,38,2],[38,3,38,6],[38,7,38,9],[38,10,38,13],[38,14,38,17],[39,1,39,2],[39,3,39,6],[39,7,39,9],[39,10,39,13],[39,14,39,17],[40,1,40,2],[40,3,40,6],[40,7,40,9],[40,10,40,13],[40,14,40,17],[41,1,41,2],[41,3,41,6],[41,7,41,9],[41,10,41,13],[41,14,41,17],[42,1,42,2],[42,3,42,6],[42,7,42,9],[42,10,42,13],[42,14,42,17],[43,1,43,2],[43,3,43,6],[43,7,43,9],[43,10,43,17],[44,1,44,2],[44,3,44,6],[44,7,44,9],[44,10,45,17],[45,1,45,2],[45,3,45,6],[45,7,45,9],[46,1,46,2],[46,3,46,6],[46,7,46,9],[46,10,48,17],[47,1,47,2],[47,3,47,6],[47,7,47,9],[48,1,48,2],[48,4,48,6],[48,7,48,9],[49,1,49,2],[49,4,49,6],[49,7,50,9],[49,10,49,13],[49,14,49,17],[50,1,50,2],[50,4,50,6],[50,10,50,13],[50,14,50,17],[51,1,51,2],[51,3,51,6],[51,7,51,9],[51,10,51,13],[51,14,51,17],[52,1,52,2],[52,3,52,6],[52,7,52,9],[52,10,52,13],[52,14,52,17],[53,1,53,2],[53,3,53,6],[53,7,53,9],[53,10,53,13],[53,14,53,17],[54,1,55,6],[54,7,55,9],[54,10,54,13],[54,14,54,17],[55,10,55,13],[55,14,55,17],[56,1,56,6],[56,7,56,9],[56,10,56,13],[56,14,56,17],[57,1,58,6],[57,7,58,9],[57,10,57,13],[57,14,57,17],[58,10,58,13],[58,14,58,17],[59,1,60,6],[59,7,60,9],[59,10,59,13],[59,14,59,17],[60,10,60,13],[60,14,60,17],[61,1,62,6],[61,7,62,9],[61,10,61,17],[62,10,62,13],[62,14,62,17],[63,1,63,2],[63,3,63,6],[63,7,64,9],[63,10,63,13],[63,14,63,17],[64,1,64,2],[64,3,64,6],[64,10,64,13],[64,14,64,17],[65,1,65,2],[65,4,65,6],[65,7,66,9],[65,10,65,13],[65,14,65,17],[66,1,66,2],[66,4,66,6],[66,10,66,13],[66,14,66,17],[67,1,67,2],[67,4,67,6],[67,7,68,9],[67,10,67,13],[67,14,67,17],[68,1,68,2],[68,4,68,6],[68,10,68,13],[68,14,68,17],[69,1,69,2],[69,4,69,6],[69,7,70,9],[69,10,69,13],[69,14,69,17],[70,1,70,2],[70,4,70,6],[70,10,70,13],[70,14,70,17],[71,1,71,2],[71,4,71,6],[71,7,71,9],[71,10,71,17],[72,1,72,2],[72,4,72,6],[72,7,72,9],[72,10,72,13],[72,14,72,17],[73,1,73,2],[73,4,73,6],[73,7,73,9],[73,10,73,13],[73,14,73,17],[74,1,74,2],[74,4,74,6],[74,7,74,9],[74,10,74,13],[74,14,74,17],[75,1,75,2],[75,4,75,6],[75,7,75,9],[75,10,75,13],[75,14,75,17],[76,1,76,2],[76,4,76,6],[76,7,76,9],[76,10,76,13],[76,14,76,17],[77,1,77,2],[77,4,77,6],[77,7,77,9],[77,10,77,13],[77,14,77,17],[78,1,78,2],[78,4,78,6],[78,7,78,9],[78,10,78,13],[78,14,78,17],[79,1,79,2],[79,3,79,6],[79,7,79,9],[79,10,79,13],[79,14,79,17],[80,1,80,2],[80,3,80,6],[80,7,80,9],[80,10,80,13],[80,14,80,17],[81,1,81,2],[81,3,81,6],[81,7,81,9],[81,10,81,13],[81,14,81,17],[82,1,82,2],[82,3,82,6],[82,7,82,9],[82,10,82,17],[83,1,83,2],[83,3,83,6],[83,7,83,9],[83,10,83,13],[83,14,83,17],[84,1,84,2],[84,3,84,6],[84,7,84,9],[84,10,84,13],[84,14,84,17],[85,1,85,2],[85,3,85,6],[85,7,85,9],[85,10,85,13],[85,14,85,17],[86,1,86,2],[86,3,86,6],[86,7,86,9],[86,10,86,13],[86,14,86,17],[87,1,87,2],[87,3,87,6],[87,7,87,9],[87,10,87,13],[87,14,87,17],[88,1,88,2],[88,3,88,6],[88,7,88,9],[88,10,88,13],[88,14,88,17],[89,1,89,2],[89,3,89,6],[89,7,89,9],[89,10,89,13],[89,14,89,17],[90,1,90,2],[90,3,90,6],[90,7,90,9],[90,10,90,13],[90,14,90,17],[91,1,91,2],[91,3,91,6],[91,7,91,9],[91,10,91,13],[91,14,91,17],[92,1,92,2],[92,3,92,6],[92,7,92,9],[92,10,92,13],[92,14,92,17],[93,1,93,2],[93,3,93,6],[93,7,93,9],[93,10,93,17],[94,1,94,2],[94,3,94,6],[94,7,94,9],[94,10,95,17],[95,1,95,2],[95,3,95,6],[95,7,95,9],[96,1,96,2],[96,3,96,6],[96,7,96,9],[96,10,98,17],[97,1,97,2],[97,3,97,6],[97,7,97,9],[98,1,98,2],[98,4,98,6],[98,7,98,9],[99,1,99,2],[99,4,99,6],[99,7,100,9],[99,10,99,13],[99,14,99,17],[100,1,100,2],[100,4,100,6],[100,10,100,13],[100,14,100,17],[101,1,101,2],[101,3,101,6],[101,7,101,9],[101,10,101,13],[101,14,101,17],[102,1,102,2],[102,3,102,6],[102,7,102,9],[102,10,102,13],[102,14,102,17],[103,1,103,2],[103,3,103,6],[103,7,103,9],[103,10,103,13],[103,14,103,17],[104,1,105,6],[104,7,105,9],[104,10,104,13],[104,14,104,17],[105,10,105,13],[105,14,105,17],[106,1,106,6],[106,7,106,9],[106,10,106,13],[106,14,106,17],[107,1,108,6],[107,7,108,9],[107,10,107,13],[107,14,107,17],[108,10,108,13],[108,14,108,17],[109,1,110,6],[109,7,110,9],[109,10,109,13],[109,14,109,17],[110,10,110,13],[110,14,110,17],[111,1,112,6],[111,7,112,9],[111,10,111,17],[112,10,112,13],[112,14,112,17],[113,1,113,2],[113,3,113,6],[113,7,114,9],[113,10,113,13],[113,14,113,17],[114,1,114,2],[114,3,114,6],[114,10,114,13],[114,14,114,17],[115,1,115,2],[115,4,115,6],[115,7,116,9],[115,10,115,13],[115,14,115,17],[116,1,116,2],[116,4,116,6],[116,10,116,13],[116,14,116,17],[117,1,117,2],[117,4,117,6],[117,7,118,9],[117,10,117,13],[117,14,117,17],[118,1,118,2],[118,4,118,6],[118,10,118,13],[118,14,118,17],[119,1,119,2],[119,4,119,6],[119,7,120,9],[119,10,119,13],[119,14,119,17],[120,1,120,2],[120,4,120,6],[120,10,120,13],[120,14,120,17],[121,1,121,2],[121,4,121,6],[121,7,121,9],[121,10,121,17],[122,1,122,2],[122,4,122,6],[122,7,122,9],[122,10,122,13],[122,14,122,17],[123,1,123,2],[123,4,123,6],[123,7,123,9],[123,10,123,13],[123,14,123,17],[124,1,124,2],[124,4,124,6],[124,7,124,9],[124,10,124,13],[124,14,124,17],[125,1,125,2],[125,4,125,6],[125,7,125,9],[125,10,125,13],[125,14,125,17],[126,1,126,2],[126,4,126,6],[126,7,126,9],[126,10,126,13],[126,14,126,17],[127,1,127,2],[127,4,127,6],[127,7,127,9],[127,10,127,13],[127,14,127,17],[128,1,128,2],[128,4,128,6],[128,7,128,9],[128,10,128,13],[128,14,128,17],[129,1,129,2],[129,3,129,6],[129,7,129,9],[129,10,129,13],[129,14,129,17],[130,1,130,2],[130,3,130,6],[130,7,130,9],[130,10,130,13],[130,14,130,17],[131,1,131,2],[131,3,131,6],[131,7,131,9],[131,10,131,13],[131,14,131,17],[132,1,132,2],[132,3,132,6],[132,7,132,9],[132,10,132,17],[133,1,133,2],[133,3,133,6],[133,7,133,9],[133,10,133,13],[133,14,133,17],[134,1,134,2],[134,3,134,6],[134,7,134,9],[134,10,134,13],[134,14,134,17],[135,1,135,2],[135,3,135,6],[135,7,135,9],[135,10,135,13],[135,14,135,17],[136,1,136,2],[136,3,136,6],[136,7,136,9],[136,10,136,13],[136,14,136,17],[137,1,137,2],[137,3,137,6],[137,7,137,9],[137,10,137,13],[137,14,137,17],[138,1,138,2],[138,3,138,6],[138,7,138,9],[138,10,138,13],[138,14,138,17],[139,1,139,2],[139,3,139,6],[139,7,139,9],[139,10,139,13],[139,14,139,17],[140,1,140,2],[140,3,140,6],[140,7,140,9],[140,10,140,13],[140,14,140,17],[141,1,141,2],[141,3,141,6],[141,7,141,9],[141,10,141,13],[141,14,141,17],[142,1,142,2],[142,3,142,6],[142,7,142,9],[142,10,142,13],[142,14,142,17],[143,1,143,2],[143,3,143,6],[143,7,143,9],[143,10,143,17],[144,1,144,2],[144,3,144,6],[144,7,144,9],[144,10,145,17],[145,1,145,2],[145,3,145,6],[145,7,145,9],[146,1,146,2],[146,3,146,6],[146,7,146,9],[146,10,148,17],[147,1,147,2],[147,3,147,6],[147,7,147,9],[148,1,148,2],[148,4,148,6],[148,7,148,9],[149,1,149,2],[149,4,149,6],[149,7,150,9],[149,10,149,13],[149,14,149,17],[150,1,150,2],[150,4,150,6],[150,10,150,13],[150,14,150,17],[151,1,151,2],[151,3,151,6],[151,7,151,9],[151,10,151,13],[151,14,151,17],[152,1,152,2],[152,3,152,6],[152,7,152,9],[152,10,152,13],[152,14,152,17],[153,1,153,2],[153,3,153,6],[153,7,153,9],[153,10,153,13],[153,14,153,17]]}
[{"$nulls":8},"气动调节阀（2、3、5工序）\nCONTROL VALVE( PNEUMATIC)"]
["项目名称\nPROJECT",null,"数智化改造项目-自动化升级改造",null,null,"图号\nDWG.NO.",null,null,"20243701-5-ZK-04-04",{"$nulls":4},"设计\nDES.","崔建峰"]
["用户\nCLIENT",null,"重庆聚狮新材料科技有限公司",null,null,"设计阶段\nSTAGE",null,null,"施工图",null,"版次\nREV.",0,null,"校核\nCHK.","袁华"]
["装置/主项\nDEVICE/SUBJECT",null,"共计：7台",null,null,"专业\nSPECIALTY",null,null,"自控",null,"工程编号\nPNO.",20243701,null,"审核\nAPPD.","李俊民"]
[1,"位号 TAG NO.",{"$nulls":5},"1TV-3(101~501)",null,null,"阀盖形式 Bonnet Type",{"$nulls":3},"供应商填写"]
[2,{"$nulls":9},"允许最大压差 Allow △P Mpa(G)",{"$nulls":3},"供应商填写"]
[3,"数量 Q'ty",{"$nulls":5},5,null,null,"最大开度 Open %AT MAX.Flow",{"$nulls":3},"供应商填写"]
[4,"用途   Service",{"$nulls":5},"1D3（101~501盘式干燥机出口温度调节",null,null,"计算CV  CALC.Cv",{"$nulls":3},"供应商填写"]
[5,{"$nulls":9},"选择CV Selected Cv",{"$nulls":3},"供应商填写"]
[6,"P&ID号 P&ID NO",{"$nulls":5},"20241215-03-GY-03- 02A",null,null,"连接形式 Connection Type",{"$nulls":3},"法兰式"]
[7]
[8,"管道或设备号 LINE ＆ EQUIP.NO.",{"$nulls":5},"1LS4-3101-100-C3C-H",null,null,"执行机构 Actuator"]
[9,{"$nulls":9},"型号 Model"]
[10,"流体参数",null,"介质 ",{"$nulls":3},"蒸汽",null,null,"型式 Type",{"$nulls":3},"气动薄膜式"]
[11,"Fluid data",null,"Fluid",{"$nulls":6},"作用形式 Action Style",{"$nulls":3},"气开"]
[12,null,null,"压力","阀前压力",null,null,0.4,null,null,"弹簧范围 Spring Range",{"$nulls":3},"80~240KPa"]
[13,null,null,"Press","Upstream Pressure",{"$nulls":5},"行程 Travel"]
[14,{"$nulls":3},"阀后压力",null,null,0.35,null,null,"手轮 Hand Wheel",{"$nulls":3},"YES"]
[15,{"$nulls":3},"Downstream Pressure",{"$nulls":5},"供气压力 Air Supply Press",{"$nulls":3},"400Kpa"]
[16,{"$nulls":3},"阀关闭压差",null,null,0.5,null,null,"气信号接口尺寸 PNEU.CONN.Size",{"$nulls":3},"1/4\"NPT"]
[17,{"$nulls":3},"Shut-off Diff Pressure"]
[18,{"$nulls":3},"单位 Unit",null,null,"Mpa(G)",null,null,"定位器 Positioner"]
[19,null,null,"温度 Temp.","操作Oper.",null,null,152,null,null,"型号 Model",{"$nulls":3},"智能型"]
[20,null,null,"  (Deg. C)","设计Des.",{"$nulls":5},"输入信号 Input signal.",{"$nulls":3},"4~20mA+HART"]
[21,null,null,"密度 Density","操作Oper.",null,null,"2.67kg/m3",null,null,"输出信号 Output signal."]
[22,null,null,"流量","最小 Min.",null,null,200,null,null,"作用形式 Action Style",{"$nulls":3},"单作用"]
[23,null,null,"Flow rate","正常 Nor.",null,null,"1000-1200",null,null,"电气接口尺寸 Cable Connection",{"$nulls":3},"1/2\"NPT"]
[24,{"$nulls":3},"最大 Max.",null,null,2000,null,null,"气源压力 Air Supply Pressure",{"$nulls":3},"400~500Kpa"]
[25,{"$nulls":3},"单位 Unit",null,null,"kg/h",null,null,"气源接口尺寸 Ca Air Conn.Size",{"$nulls":3},"1/4\"NPT"]
[26,null,null,"管道规格 Specification",{"$nulls":3},"DN100",null,null,"防护等级 Protection Class",{"$nulls":3},"IP65"]
[27,null,null,"管道材料 Material",{"$nulls":3},"20#",null,null,"防爆等级 Ex.Certification",{"$nulls":3},"ExdIIBT4"]
[28,null,null,"动力粘度 Viscosity  (CP)",{"$nulls":3},0.14]
[29,null,null,"压缩系数 Compress Factor",{"$nulls":6},"附件 Accessories"]
[30,null,null,"气化压力 Vapor Pressure Mpa",{"$nulls":6},"过滤减压阀 Regulator ",{"$nulls":3},"带 1/4\"NPT(F)-φ8"]
[31,null,null,"临界压力 Critical Press Mpa",{"$nulls":6},"限位开关 Limited Switch "]
[32,null,null,"噪音 Noise Level",{"$nulls":6},"电磁阀 Solenoid valve"]
[33,null,null,"气源故障阀开/关 FO/FC",{"$nulls":3},"FC",null,null,"电源 Power Supply"]
[34,"阀体/阀芯规格 ",null,"型号 Model",{"$nulls":6},"防爆等级 Ex.Certification"]
[35,"Body/Plug ",null,"阀形式 Valve Style",{"$nulls":3},"单座调节阀（笼式平衡调节阀）",null,null,"电气接口尺寸 ELEC.CONN.Size"]
[36,"Specification",null,"流开/流关 Flow Open/Close",{"$nulls":6},"保位阀 Locked Valve"]
[37,null,null,"阀座数量 Seat NO.",{"$nulls":3},1,null,null,"备用钢瓶 Spare Cylinder"]
[38,null,null,"阀芯形式 Plug Type",{"$nulls":3},"单座柱塞型",null,null,"制造厂 Manufacturer"]
[39,null,null,"阀口径 Port size",{"$nulls":3},"供应商填写"]
[40,null,null,"流量特性 Flow Characteristic",{"$nulls":3},"等百分比",null,null,"备注 Remarks"]
[41,null,null,"阀体材质 Body Material",{"$nulls":3},"WCB",null,null,"阀门口径、内件、气源接口尺寸等的选择以最终确定的供货商设计计算选型为准。"]
[42,null,null,"阀芯材质 Plug Material",{"$nulls":3},"304+ST"]
[43,null,null,"阀座材质 Seat Material",{"$nulls":3},"304+ST",null,null,"带符合工艺及仪表要求的配对法兰，垫片(RSB)、紧固件及其它阀内安装附件。"]
[44,null,null,"阀杆材质 Stem Material",{"$nulls":3},316]
[45,null,null,"连接尺寸","尺寸  Size",null,null,{"$f":"H30","v":"DN100"}]
[46,null,null,"Process","标准 Rating",null,null,"HG20592-2009(B) PN16 SO-RF"]
[47,null,null,"connection"]
[48,null,null,"法兰材质 Flange Material",{"$nulls":3},"同阀体"]
[49,null,null,"填料 Packing",{"$nulls":3},"柔性石墨"]
[50,null,null,"泄漏等级 Leakage Class",{"$nulls":3},"ANSI V"]
[1,"位号 TAG NO.",{"$nulls":5},"1LV-2005",null,null,"阀盖形式 Bonnet Type",{"$nulls":3},"供应商填写"]
[2,{"$nulls":9},"允许最大压差 Allow △P Mpa(G)",{"$nulls":3},"供应商填写"]
[3,"数量 Q'ty",{"$nulls":5},1,null,null,"最大开度 Open %AT MAX.Flow",{"$nulls":3},"供应商填写"]
[4,"用途   Service",{"$nulls":5},"1V2005洗水高位槽补水液位调节",null,null,"计算CV  CALC.Cv",{"$nulls":3},"供应商填写"]
[5,{"$nulls":9},"选择CV Selected Cv",{"$nulls":3},"供应商填写"]
[6,"P&ID号 P&ID NO",{"$nulls":5},"20241215-02-GY-03- 01",null,null,"连接形式 Connection Type",{"$nulls":3},"法兰式"]
[7]
[8,"管道或设备号 LINE ＆ EQUIP.NO.",{"$nulls":5},"1DW-2002-80-C1S-N",null,null,"执行机构 Actuator"]
[9,{"$nulls":9},"型号 Model"]
[10,"流体参数",null,"介质 ",{"$nulls":3},"洗水（极少量PPS小颗粒，Cl-）",null,null,"型式 Type",{"$nulls":3},"气动薄膜式"]
[11,"Fluid data",null,"Fluid",{"$nulls":6},"作用形式 Action Style",{"$nulls":3},"气开"]
[12,null,null,"压力","阀前压力",null,null,0.4,null,null,"弹簧范围 Spring Range",{"$nulls":3},"80~240KPa"]
[13,null,null,"Press","Upstream Pressure",{"$nulls":5},"行程 Travel"]
[14,{"$nulls":3},"阀后压力",null,null,0.35,null,null,"手轮 Hand Wheel",{"$nulls":3},"YES"]
[15,{"$nulls":3},"Downstream Pressure",{"$nulls":5},"供气压力 Air Supply Press",{"$nulls":3},"400Kpa"]
[16,{"$nulls":3},"阀关闭压差",null,null,0.5,null,null,"气信号接口尺寸 PNEU.CONN.Size",{"$nulls":3},"1/4\"NPT"]
[17,{"$nulls":3},"Shut-off Diff Pressure"]
[18,{"$nulls":3},"单位 Unit",null,null,"Mpa(G)",null,null,"定位器 Positioner"]
[19,null,null,"温度 Temp.","操作Oper.",null,null,60,null,null,"型号 Model",{"$nulls":3},"智能型"]
[20,null,null,"  (Deg. C)","设计Des.",{"$nulls":5},"输入信号 Input signal.",{"$nulls":3},"4~20mA+HART"]
[21,null,null,"密度 Density","操作Oper.",null,null,"1000kg/m3",null,null,"输出信号 Output signal."]
[22,null,null,"流量","最小 Min.",null,null,18,null,null,"作用形式 Action Style",{"$nulls":3},"单作用"]
[23,null,null,"Flow rate","正常 Nor.",null,null,30,null,null,"电气接口尺寸 Cable Connection",{"$nulls":3},"1/2\"NPT"]
[24,{"$nulls":3},"最大 Max.",null,null,36,null,null,"气源压力 Air Supply Pressure",{"$nulls":3},"400~500Kpa"]
[25,{"$nulls":3},"单位 Unit",null,null,"m3/h",null,null,"气源接口尺寸 Ca Air Conn.Size",{"$nulls":3},"1/4\"NPT"]
[26,null,null,"管道规格 Specification",{"$nulls":3},"DN80",null,null,"防护等级 Protection Class",{"$nulls":3},"IP65"]
[27,null,null,"管道材料 Material",{"$nulls":3},"S30408",null,null,"防爆等级 Ex.Certification",{"$nulls":3},"ExdIIBT4"]
[28,null,null,"动力粘度 Viscosity  (CP)",{"$nulls":3},0.84]
[29,null,null,"压缩系数 Compress Factor",{"$nulls":6},"附件 Accessories"]
[30,null,null,"气化压力 Vapor Pressure Mpa",{"$nulls":6},"过滤减压阀 Regulator ",{"$nulls":3},"带 1/4\"NPT(F)-φ8"]
[31,null,null,"临界压力 Critical Press Mpa",{"$nulls":6},"限位开关 Limited Switch "]
[32,null,null,"噪音 Noise Level",{"$nulls":6},"电磁阀 Solenoid valve"]
[33,null,null,"气源故障阀开/关 FO/FC",{"$nulls":3},"FC",null,null,"电源 Power Supply"]
[34,"阀体/阀芯规格 ",null,"型号 Model",{"$nulls":6},"防爆等级 Ex.Certification"]
[35,"Body/Plug ",null,"阀形式 Valve Style",{"$nulls":3},"单座调节阀",null,null,"电气接口尺寸 ELEC.CONN.Size"]
[36,"Specification",null,"流开/流关 Flow Open/Close",{"$nulls":6},"保位阀 Locked Valve"]
[37,null,null,"阀座数量 Seat NO.",{"$nulls":3},1,null,null,"备用钢瓶 Spare Cylinder"]
[38,null,null,"阀芯形式 Plug Type",{"$nulls":3},"单座柱塞型",null,null,"制造厂 Manufacturer"]
[39,null,null,"阀口径 Port size",{"$nulls":3},"供应商填写"]
[40,null,null,"流量特性 Flow Characteristic",{"$nulls":3},"等百分比",null,null,"备注 Remarks"]
[41,null,null,"阀体材质 Body Material",{"$nulls":3},"CF8",null,null,"阀门口径、内件、气源接口尺寸等的选择以最终确定的供货商设计计算选型为准。"]
[42,null,null,"阀芯材质 Plug Material",{"$nulls":3},304]
[43,null,null,"阀座材质 Seat Material",{"$nulls":3},304,null,null,"带符合工艺及仪表要求的配对法兰，垫片(RPTFE)、紧固件及其它阀内安装附件。"]
[44,null,null,"阀杆材质 Stem Material",{"$nulls":3},316]
[45,null,null,"连接尺寸","尺寸  Size",null,null,{"$f":"H80","v":"DN80"}]
[46,null,null,"Process","标准 Rating",null,null,"HG20592-2009(B) PN16 SO-RF"]
[47,null,null,"connection"]
[48,null,null,"法兰材质 Flange Material",{"$nulls":3},"同阀体"]
[49,null,null,"填料 Packing",{"$nulls":3},"PTFE"]
[50,null,null,"泄漏等级 Leakage Class",{"$nulls":3},"ANSI V"]
[1,"位号 TAG NO.",{"$nulls":5},"1LV-2504",null,null,"阀盖形式 Bonnet Type",{"$nulls":3},"供应商填写"]
[2,{"$nulls":9},"允许最大压差 Allow △P Mpa(G)",{"$nulls":3},"供应商填写"]
[3,"数量 Q'ty",{"$nulls":5},1,null,null,"最大开度 Open %AT MAX.Flow",{"$nulls":3},"供应商填写"]
[4,"用途   Service",{"$nulls":5},"1V9002B洗液溢流槽补水液位调节",null,null,"计算CV  CALC.Cv",{"$nulls":3},"供应商填写"]
[5,{"$nulls":9},"选择CV Selected Cv",{"$nulls":3},"供应商填写"]
[6,"P&ID号 P&ID NO",{"$nulls":5},"20241215-02-GY-03- 02E",null,null,"连接形式 Connection Type",{"$nulls":3},"法兰式"]
[7]
[8,"管道或设备号 LINE ＆ EQUIP.NO.",{"$nulls":5},"1DW-2501-50-C2S-N",null,null,"执行机构 Actuator"]
[9,{"$nulls":9},"型号 Model"]
[10,"流体参数",null,"介质 ",{"$nulls":3},"脱盐水",null,null,"型式 Type",{"$nulls":3},"气动薄膜式"]
[11,"Fluid data",null,"Fluid",{"$nulls":6},"作用形式 Action Style",{"$nulls":3},"气开"]
[12,null,null,"压力","阀前压力",null,null,0.4,null,null,"弹簧范围 Spring Range",{"$nulls":3},"80~240KPa"]
[13,null,null,"Press","Upstream Pressure",{"$nulls":5},"行程 Travel"]
[14,{"$nulls":3},"阀后压力",null,null,0.35,null,null,"手轮 Hand Wheel",{"$nulls":3},"YES"]
[15,{"$nulls":3},"Downstream Pressure",{"$nulls":5},"供气压力 Air Supply Press",{"$nulls":3},"400Kpa"]
[16,{"$nulls":3},"阀关闭压差",null,null,0.5,null,null,"气信号接口尺寸 PNEU.CONN.Size",{"$nulls":3},"1/4\"NPT"]
[17,{"$nulls":3},"Shut-off Diff Pressure"]
[18,{"$nulls":3},"单位 Unit",null,null,"Mpa(G)",null,null,"定位器 Positioner"]
[19,null,null,"温度 Temp.","操作Oper.",null,null,"常温",null,null,"型号 Model",{"$nulls":3},"智能型"]
[20,null,null,"  (Deg. C)","设计Des.",{"$nulls":5},"输入信号 Input signal.",{"$nulls":3},"4~20mA+HART"]
[21,null,null,"密度 Density","操作Oper.",null,null,"1000kg/m3",null,null,"输出信号 Output signal."]
[22,null,null,"流量","最小 Min.",null,null,7.2,null,null,"作用形式 Action Style",{"$nulls":3},"单作用"]
[23,null,null,"Flow rate","正常 Nor.",null,null,12,null,null,"电气接口尺寸 Cable Connection",{"$nulls":3},"1/2\"NPT"]
[24,{"$nulls":3},"最大 Max.",null,null,14.4,null,null,"气源压力 Air Supply Pressure",{"$nulls":3},"400~500Kpa"]
[25,{"$nulls":3},"单位 Unit",null,null,"m3/h",null,null,"气源接口尺寸 Ca Air Conn.Size",{"$nulls":3},"1/4\"NPT"]
[26,null,null,"管道规格 Specification",{"$nulls":3},"DN50",null,null,"防护等级 Protection Class",{"$nulls":3},"IP65"]
[27,null,null,"管道材料 Material",{"$nulls":3},"S30408",null,null,"防爆等级 Ex.Certification",{"$nulls":3},"ExdIIBT4"]
[28,null,null,"动力粘度 Viscosity  (CP)",{"$nulls":3},0.84]
[29,null,null,"压缩系数 Compress Factor",{"$nulls":6},"附件 Accessories"]
[30,null,null,"气化压力 Vapor Pressure Mpa",{"$nulls":6},"过滤减压阀 Regulator ",{"$nulls":3},"带 1/4\"NPT(F)-φ8"]
[31,null,null,"临界压力 Critical Press Mpa",{"$nulls":6},"限位开关 Limited Switch "]
[32,null,null,"噪音 Noise Level",{"$nulls":6},"电磁阀 Solenoid valve"]
[33,null,null,"气源故障阀开/关 FO/FC",{"$nulls":3},"FC",null,null,"电源 Power Supply"]
[34,"阀体/阀芯规格 ",null,"型号 Model",{"$nulls":6},"防爆等级 Ex.Certification"]
[35,"Body/Plug ",null,"阀形式 Valve Style",{"$nulls":3},"单座调节阀",null,null,"电气接口尺寸 ELEC.CONN.Size"]
[36,"Specification",null,"流开/流关 Flow Open/Close",{"$nulls":6},"保位阀 Locked Valve"]
[37,null,null,"阀座数量 Seat NO.",{"$nulls":3},1,null,null,"备用钢瓶 Spare Cylinder"]
[38,null,null,"阀芯形式 Plug Type",{"$nulls":3},"单座柱塞型",null,null,"制造厂 Manufacturer"]
[39,null,null,"阀口径 Port size",{"$nulls":3},"供应商填写"]
[40,null,null,"流量特性 Flow Characteristic",{"$nulls":3},"等百分比",null,null,"备注 Remarks"]
[41,null,null,"阀体材质 Body Material",{"$nulls":3},"CF8",null,null,"阀门口径、内件、气源接口尺寸等的选择以最终确定的供货商设计计算选型为准。"]
[42,null,null,"阀芯材质 Plug Material",{"$nulls":3},304]
[43,null,null,"阀座材质 Seat Material",{"$nulls":3},304,null,null,"带符合工艺及仪表要求的配对法兰，垫片(RPTFE)、紧固件及其它阀内安装附件。"]
[44,null,null,"阀杆材质 Stem Material",{"$nulls":3},316]
[45,null,null,"连接尺寸","尺寸  Size",null,null,{"$f":"H130","v":"DN50"}]
[46,null,null,"Process","标准 Rating",null,null,"HG20592-2009(B) PN16 SO-RF"]
[47,null,null,"connection"]
[48,null,null,"法兰材质 Flange Material",{"$nulls":3},"同阀体"]
[49,null,null,"填料 Packing",{"$nulls":3},"PTFE"]
[50,null,null,"泄漏等级 Leakage Class",{"$nulls":3},"ANSI V"]

{"sheet":"05）切断阀","index":1,"n_rows":1254,"n_cols":15,"rows_kept":1254,"merged":[[0,8,0,17],[1,0,1,1],[1,2,1,4],[1,5,1,7],[1,8,1,12],[1,14,1,16],[2,0,2,1],[2,2,2,4],[2,5,2,7],[2,8,2,9],[2,11,2,12],[2,14,2,16],[3,0,3,1],[3,2,3,4],[3,5,3,7],[3,8,3,9],[3,11,3,12],[3,14,3,16],[4,10,4,13],[4,14,4,17],[5,10,5,13],[5,14,5,17],[6,1,6,6],[6,7,6,9],[6,10,6,13],[6,14,6,17],[7,10,7,13],[7,14,7,17],[8,10,8,13],[8,14,8,17],[9,10,9,13],[9,14,9,17],[10,10,10,13],[10,14,10,17],[11,10,11,17],[12,10,12,13],[12,14,12,17],[13,1,13,2],[13,3,13,6],[13,10,13,13],[13,14,13,17],[14,1,14,2],[14,3,14,6],[14,10,14,13],[14,14,14,17],[15,1,15,2],[15,4,15,6],[15,10,15,13],[15,14,15,17],[16,1,16,2],[16,4,16,6],[16,10,16,13],[16,14,16,17],[17,1,17,2],[17,4,17,6],[17,10,17,13],[17,14,17,17],[18,1,18,2],[18,4,18,6],[18,10,18,13],[18,14,18,17],[19,1,19,2],[19,4,19,6],[19,10,19,13],[19,14,19,17],[20,1,20,2],[20,4,20,6],[20,10,20,13],[20,14,20,17],[21,1,21,2],[21,4,21,6],[21,7,21,9],[21,10,21,17],[22,1,22,2],[22,4,22,6],[22,7,22,9],[22,10,22,13],[22,14,22,17],[23,1,23,2],[23,4,23,6],[23,7,23,9],[23,10,23,13],[23,14,23,17],[24,1,24,2],[24,4,24,6],[24,7,24,9],[24,10,24,13],[24,14,24,17],[25,1,25,2],[25,4,25,6],[25,7,25,9],[25,10,25,13],[25,14,25,17],[26,1,26,2],[26,4,26,6],[26,7,26,9],[26,10,26,13],[26,14,26,17],[27,1,27,2],[27,4,27,6],[27,7,27,9],[27,10,27,13],[27,14,27,17],[28,1,28,2],[28,4,28,6],[28,7,28,9],[28,10,28,13],[28,14,28,17],[29,1,29,2],[29,3,29,6],[29,7,29,9],[29,10,29,13],[29,14,29,17],[30,1,30,2],[30,3,30,6],[30,7,30,9],[30,10,30,13],[30,14,30,17],[31,1,31,2],[31,3,31,6],[31,7,31,9],[31,10,31,13],[31,14,31,17],[32,1,32,2],[32,3,32,6],[32,7,32,9],[32,10,32,17],[33,1,33,2],[33,3,33,6],[33,7,33,9],[34,1,34,2],[34,3,34,6],[34,7,34,9],[35,1,35,2],[35,3,35,6],[35,7,35,9],[36,1,36,2],[36,3,36,6],[36,7,36,9],[37,1,37,2],[37,3,37,6],[37,7,37,9],[38,1,38,2],[38,3,38,6],[38,7,38,9],[38,10,38,13],[38,14,38,17],[39,1,39,2],[39,3,39,6],[39,7,39,9],[39,10,39,13],[39,14,39,17],[40,1,40,2],[40,3,40,6],[40,7,40,9],[40,10,40,13],[40,14,40,17],[41,1,41,2],[41,3,41,6],[41,7,41,9],[41,10,41,13],[41,14,41,17],[42,1,42,2],[42,3,42,6],[42,7,42,9],[42,10,42,13],[42,14,42,17],[43,1,43,2],[43,3,43,6],[43,7,43,9],[43,10,43,13],[43,14,43,17],[44,1,44,2],[44,3,44,6],[44,7,44,9],[44,10,44,13],[44,14,44,17],[45,1,45,2],[45,3,45,6],[45,7,45,9],[45,10,45,13],[45,14,45,17],[46,1,46,2],[46,3,46,6],[46,7,46,9],[46,10,46,13],[46,14,46,17],[47,1,47,2],[47,3,47,6],[47,7,47,9],[47,10,47,13],[47,14,47,17],[48,1,48,2],[48,4,48,6],[48,7,48,9],[48,10,48,13],[48,14,48,17],[49,1,49,2],[49,4,49,6],[49,10,49,13],[49,14,49,17],[50,1,50,2],[50,4,50,6],[50,10,50,13],[50,14,50,17],[51,1,51,2],[51,3,51,6],[51,7,51,9],[51,10,51,13],[51,14,51,17],[52,1,52,2],[52,3,52,6],[52,7,52,9],[52,10,52,13],[52,14,52,17],[53,1,53,2],[53,3,53,6],[53,7,53,9],[53,10,53,13],[53,14,53,17],[54,10,54,13],[54,14,54,17],[55,10,55,13],[55,14,55,17],[56,1,56,6],[56,7,56,9],[56,10,56,13],[56,14,56,17],[57,10,57,13],[57,14,57,17],[58,10,58,13],[58,14,58,17],[59,10,59,13],[59,14,59,17],[60,10,60,13],[60,14,60,17],[61,10,61,17],[62,10,62,13],[62,14,62,17],[63,1,63,2],[63,3,63,6],[63,10,63,13],[63,14,63,17],[64,1,64,2],[64,3,64,6],[64,10,64,13],[64,14,64,17],[65,1,65,2],[65,4,65,6],[65,10,65,13],[65,14,65,17],[66,1,66,2],[66,4,66,6],[66,10,66,13],[66,14,66,17],[67,1,67,2],[67,4,67,6],[67,10,67,13],[67,14,67,17],[68,1,68,2],[68,4,68,6],[68,10,68,13],[68,14,68,17],[69,1,69,2],[69,4,69,6],[69,10,69,13],[69,14,69,17],[70,1,70,2],[70,4,70,6],[70,10,70,13],[70,14,70,17],[71,1,71,2],[71,4,71,6],[71,7,71,9],[71,10,71,17],[72,1,72,2],[72,4,72,6],[72,7,72,9],[72,10,72,13],[72,14,72,17],[73,1,73,2],[73,4,73,6],[73,7,73,9],[73,10,73,13],[73,14,73,17],[74,1,74,2],[74,4,74,6],[74,7,74,9],[74,10,74,13],[74,14,74,17],[75,1,75,2],[75,4,75,6],[75,7,75,9],[75,10,75,13],[75,14,75,17],[76,1,76,2],[76,4,76,6],[76,7,76,9],[76,10,76,13],[76,14,76,17],[77,1,77,2],[77,4,77,6],[77,7,77,9],[77,10,77,13],[77,14,77,17],[78,1,78,2],[78,4,78,6],[78,7,78,9],[78,10,78,13],[78,14,78,17],[79,1,79,2],[79,3,79,6],[79,7,79,9],[79,10,79,13],[79,14,79,17],[80,1,80,2],[80,3,80,6],[80,7,80,9],[80,10,80,13],[80,14,80,17],[81,1,81,2],[81,3,81,6],[81,7,81,9],[81,10,81,13],[81,14,81,17],[82,1,82,2],[82,3,82,6],[82,7,82,9],[82,10,82,17],[83,1,83,2],[83,3,83,6],[83,7,83,9],[84,1,84,2],[84,3,84,6],[84,7,84,9],[85,1,85,2],[85,3,85,6],[85,7,85,9],[86,1,86,2],[86,3,86,6],[86,7,86,9],[87,1,87,2],[87,3,87,6],[87,7,87,9],[88,1,88,2],[88,3,88,6],[88,7,88,9],[88,10,88,13],[88,14,88,17],[89,1,89,2],[89,3,89,6],[89,7,89,9],[89,10,89,13],[89,14,89,17],[90,1,90,2],[90,3,90,6],[90,7,90,9],[90,10,90,13],[90,14,90,17],[91,1,91,2],[91,3,91,6],[91,7,91,9],[91,10,91,13],[91,14,91,17],[92,1,92,2],[92,3,92,6],[92,7,92,9],[92,10,92,13],[92,14,92,17],[93,1,93,2],[93,3,93,6],[93,7,93,9],[93,10,93,13],[93,14,93,17],[94,1,94,2],[94,3,94,6],[94,7,94,9],[94,10,94,13],[94,14,94,17],[95,1,95,2],[95,3,95,6],[95,7,95,9],[95,10,95,13],[95,14,95,17],[96,1,96,2],[96,3,96,6],[96,7,96,9],[96,10,96,13],[96,14,96,17],[97,1,97,2],[97,3,97,6],[97,7,97,9],[97,10,97,13],[97,14,97,17],[98,1,98,2],[98,4,98,6],[98,7,98,9],[98,10,98,13],[98,14,98,17],[99,1,99,2],[99,4,99,6],[99,10,99,13],[99,14,99,17],[100,1,100,2],[100,4,100,6],[100,10,100,13],[100,14,100,17],[101,1,101,2],[101,3,101,6],[101,7,101,9],[101,10,101,13],[101,14,101,17],[102,1,102,2],[102,3,102,6],[102,7,102,9],[102,10,102,13],[102,14,102,17],[103,1,103,2],[103,3,103,6],[103,7,103,9],[103,10,103,13],[103,14,103,17],[104,10,104,13],[104,14,104,17],[105,10,105,13],[105,14,105,17],[106,1,106,6],[106,7,106,9],[106,10,106,13],[106,14,106,17],[107,10,107,13],[107,14,107,17],[108,10,108,13],[108,14,108,17],[109,10,109,13],[109,14,109,17],[110,10,110,13],[110,14,110,17],[111,10,111,17],[112,10,112,13],[112,14,112,17],[113,1,113,2],[113,3,113,6],[113,10,113,13],[113,14,113,17],[114,1,114,2],[114,3,114,6],[114,10,114,13],[114,14,114,17],[115,1,115,2],[115,4,115,6],[115,10,115,13],[115,14,115,17],[116,1,116,2],[116,4,116,6],[116,10,116,13],[116,14,116,17],[117,1,117,2],[117,4,117,6],[117,10,117,13],[117,14,117,17],[118,1,118,2],[118,4,118,6],[118,10,118,13],[118,14,118,17],[119,1,119,2],[119,4,119,6],[119,10,119,13],[119,14,119,17],[120,1,120,2],[120,4,120,6],[120,10,120,13],[120,14,120,17],[121,1,121,2],[121,4,121,6],[121,7,121,9],[121,10,121,17],[122,1,122,2],[122,4,122,6],[122,7,122,9],[122,10,122,13],[122,14,122,17],[123,1,123,2],[123,4,123,6],[123,7,123,9],[123,10,123,13],[123,14,123,17],[124,1,124,2],[124,4,124,6],[124,7,124,9],[124,10,124,13],[124,14,124,17],[125,1,125,2],[125,4,125,6],[125,7,125,9],[125,10,125,13],[125,14,125,17],[126,1,126,2],[126,4,126,6],[126,7,126,9],[126,10,126,13],[126,14,126,17],[127,1,127,2],[127,4,127,6],[127,7,127,9],[127,10,127,13],[127,14,127,17],[128,1,128,2],[128,4,128,6],[128,7,128,9],[128,10,128,13],[128,14,128,17],[129,1,129,2],[129,3,129,6],[129,7,129,9],[129,10,129,13],[129,14,129,17],[130,1,130,2],[130,3,130,6],[130,7,130,9],[130,10,130,13],[130,14,130,17],[131,1,131,2],[131,3,131,6],[131,7,131,9],[131,10,131,13],[131,14,131,17],[132,1,132,2],[132,3,132,6],[132,7,132,9],[132,10,132,17],[133,1,133,2],[133,3,133,6],[133,7,133,9],[134,1,134,2],[134,3,134,6],[134,7,134,9],[135,1,135,2],[135,3,135,6],[135,7,135,9],[136,1,136,2],[136,3,136,6],[136,7,136,9],[137,1,137,2],[137,3,137,6],[137,7,137,9],[138,1,138,2],[138,3,138,6],[138,7,138,9],[138,10,138,13],[138,14,138,17],[139,1,139,2],[139,3,139,6],[139,7,139,9],[139,10,139,13],[139,14,139,17],[140,1,140,2],[140,3,140,6],[140,7,140,9],[140,10,140,13],[140,14,140,17],[141,1,141,2],[141,3,141,6],[141,7,141,9],[141,10,141,13],[141,14,141,17],[142,1,142,2],[142,3,142,6],[142,7,142,9],[142,10,142,13],[142,14,142,17],[143,1,143,2],[143,3,143,6],[143,7,143,9],[143,10,143,13],[143,14,143,17],[144,1,144,2],[144,3,144,6],[144,7,144,9],[144,10,144,13],[144,14,144,17],[145,1,145,2],[145,3,145,6],[145,7,145,9],[145,10,145,13],[145,14,145,17],[146,1,146,2],[146,3,146,6],[146,7,146,9],[146,10,146,13],[146,14,146,17],[147,1,147,2],[147,3,147,6],[147,7,147,9],[147,10,147,13],[147,14,147,17],[148,1,148,2],[148,4,148,6],[148,7,148,9],[148,10,148,13],[148,14,148,17],[149,1,149,2],[149,4,149,6],[149,10,149,13],[149,14,149,17],[150,1,150,2],[150,4,150,6],[150,10,150,13],[150,14,150,17],[151,1,151,2],[151,3,151,6],[151,7,151,9],[151,10,151,13],[151,14,151,17],[152,1,152,2],[152,3,152,6],[152,7,152,9],[152,10,152,13],[152,14,152,17],[153,1,153,2],[153,3,153,6],[153,7,153,9],[153,10,153,13],[153,14,153,17],[154,10,154,13],[154,14,154,17],[155,10,155,13],[155,14,155,17],[156,1,156,6],[156,7,156,9],[156,10,156,13],[156,14,156,17],[157,10,157,13],[157,14,157,17],[158,10,158,13],[158,14,158,17],[159,10,159,13],[159,14,159,17],[160,10,160,13],[160,14,160,17],[161,10,161,17],[162,10,162,13],[162,14,162,17],[163,1,163,2],[163,3,163,6],[163,10,163,13],[163,14,163,17],[164,1,164,2],[164,3,164,6],[164,10,164,13],[164,14,164,17],[165,1,165,2],[165,4,165,6],[165,10,165,13],[165,14,165,17],[166,1,166,2],[166,4,166,6],[166,10,166,13],[166,14,166,17],[167,1,167,2],[167,4,167,6],[167,10,167,13],[167,14,167,17],[168,1,168,2],[168,4,168,6],[168,10,168,13],[168,14,168,17],[169,1,169,2],[169,4,169,6],[169,10,169,13],[169,14,169,17],[170,1,170,2],[170,4,170,6],[170,10,170,13],[170,14,170,17],[171,1,171,2],[171,4,171,6],[171,7,171,9],[171,10,171,17],[172,1,172,2],[172,4,172,6],[172,7,172,9],[172,10,172,13],[172,14,172,17],[173,1,173,2],[173,4,173,6],[173,7,173,9],[173,10,173,13],[173,14,173,17],[174,1,174,2],[174,4,174,6],[174,7,174,9],[174,10,174,13],[174,14,174,17],[175,1,175,2],[175,4,175,6],[175,7,175,9],[175,10,175,13],[175,14,175,17],[176,1,176,2],[176,4,176,6],[176,7,176,9],[176,10,176,13],[176,14,176,17],[177,1,177,2],[177,4,177,6],[177,7,177,9],[177,10,177,13],[177,14,177,17],[178,1,178,2],[178,4,178,6],[178,7,178,9],[178,10,178,13],[178,14,178,17],[179,1,179,2],[179,3,179,6],[179,7,179,9],[179,10,179,13],[179,14,179,17],[180,1,180,2],[180,3,180,6],[180,7,180,9],[180,10,180,13],[180,14,180,17],[181,1,181,2],[181,3,181,6],[181,7,181,9],[181,10,181,13],[181,14,181,17],[182,1,182,2],[182,3,182,6],[182,7,182,9],[182,10,182,17],[183,1,183,2],[183,3,183,6],[183,7,183,9],[184,1,184,2],[184,3,184,6],[184,7,184,9],[185,1,185,2],[185,3,185,6],[185,7,185,9],[186,1,186,2],[186,3,186,6],[186,7,186,9],[187,1,187,2],[187,3,187,6],[187,7,187,9],[188,1,188,2],[188,3,188,6],[188,7,188,9],[188,10,188,13],[188,14,188,17],[189,1,189,2],[189,3,189,6],[189,7,189,9],[189,10,189,13],[189,14,189,17],[190,1,190,2],[190,3,190,6],[190,7,190,9],[190,10,190,13],[190,14,190,17],[191,1,191,2],[191,3,191,6],[191,7,191,9],[191,10,191,13],[191,14,191,17],[192,1,192,2],[192,3,192,6],[192,7,192,9],[192,10,192,13],[192,14,192,17],[193,1,193,2],[193,3,193,6],[193,7,193,9],[193,10,193,13],[193,14,193,17],[194,1,194,2],[194,3,194,6],[194,7,194,9],[194,10,194,13],[194,14,194,17],[195,1,195,2],[195,3,195,6],[195,7,195,9],[195,10,195,13],[195,14,195,17],[196,1,196,2],[196,3,196,6],[196,7,196,9],[196,10,196,13],[196,14,196,17],[197,1,197,2],[197,3,197,6],[197,7,197,9],[197,10,197,13],[197,14,197,17],[198,1,198,2],[198,4,198,6],[198,7,198,9],[198,10,198,13],[198,14,198,17],[199,1,199,2],[199,4,199,6],[199,10,199,13],[199,14,199,17],[200,1,200,2],[200,4,200,6],[200,10,200,13],[200,14,200,17],[201,1,201,2],[201,3,201,6],[201,7,201,9],[201,10,201,13],[201,14,201,17],[202,1,202,2],[202,3,202,6],[202,7,202,9],[202,10,202,13],[202,14,202,17],[203,1,203,2],[203,3,203,6],[203,7,203,9],[203,10,203,13],[203,14,203,17],[204,10,204,13],[204,14,204,17],[205,10,205,13],[205,14,205,17],[206,1,206,6],[206,7,206,9],[206,10,206,13],[206,14,206,17],[207,10,207,13],[207,14,207,17],[208,10,208,13],[208,14,208,17],[209,10,209,13],[209,14,209,17],[210,10,210,13],[210,14,210,17],[211,10,211,17],[212,10,212,13],[212,14,212,17],[213,1,213,2],[213,3,213,6],[213,10,213,13],[213,14,213,17],[214,1,214,2],[214,3,214,6],[214,10,214,13],[214,14,214,17],[215,1,215,2],[215,4,215,6],[215,10,215,13],[215,14,215,17],[216,1,216,2],[216,4,216,6],[216,10,216,13],[216,14,216,17],[217,1,217,2],[217,4,217,6],[217,10,217,13],[217,14,217,17],[218,1,218,2],[218,4,218,6],[218,10,218,13],[218,14,218,17],[219,1,219,2],[219,4,219,6],[219,10,219,13],[219,14,219,17],[220,1,220,2],[220,4,220,6],[220,10,220,13],[220,14,220,17],[221,1,221,2],[221,4,221,6],[221,7,221,9],[221,10,221,17],[222,1,222,2],[222,4,222,6],[222,7,222,9],[222,10,222,13],[222,14,222,17],[223,1,223,2],[223,4,223,6],[223,7,223,9],[223,10,223,13],[223,14,223,17],[224,1,224,2],[224,4,224,6],[224,7,224,9],[224,10,224,13],[224,14,224,17],[225,1,225,2],[225,4,225,6],[225,7,225,9],[225,10,225,13],[225,14,225,17],[226,1,226,2],[226,4,226,6],[226,7,226,9],[226,10,226,13],[226,14,226,17],[227,1,227,2],[227,4,227,6],[227,7,227,9],[227,10,227,13],[227,14,227,17],[228,1,228,2],[228,4,228,6],[228,7,228,9],[228,10,228,13],[228,14,228,17],[229,1,229,2],[229,3,229,6],[229,7,229,9],[229,10,229,13],[229,14,229,17],[230,1,230,2],[230,3,230,6],[230,7,230,9],[230,10,230,13],[230,14,230,17],[231,1,231,2],[231,3,231,6],[231,7,231,9],[231,10,231,13],[231,14,231,17],[232,1,232,2],[232,3,232,6],[232,7,232,9],[232,10,232,17],[233,1,233,2],[233,3,233,6],[233,7,233,9],[234,1,234,2],[234,3,234,6],[234,7,234,9],[235,1,235,2],[235,3,235,6],[235,7,235,9],[236,1,236,2],[236,3,236,6],[236,7,236,9],[237,1,237,2],[237,3,237,6],[237,7,237,9],[238,1,238,2],[238,3,238,6],[238,7,238,9],[238,10,238,13],[238,14,238,17],[239,1,239,2],[239,3,239,6],[239,7,239,9],[239,10,239,13],[239,14,239,17],[240,1,240,2],[240,3,240,6],[240,7,240,9],[240,10,240,13],[240,14,240,17],[241,1,241,2],[241,3,241,6],[241,7,241,9],[241,10,241,13],[241,14,241,17],[242,1,242,2],[242,3,242,6],[242,7,242,9],[242,10,242,13],[242,14,242,17],[243,1,243,2],[243,3,243,6],[243,7,243,9],[243,10,243,13],[243,14,243,17],[244,1,244,2],[244,3,244,6],[244,7,244,9],[244,10,244,13],[244,14,244,17],[245,1,245,2],[245,3,245,6],[245,7,245,9],[245,10,245,13],[245,14,245,17],[246,1,246,2],[246,3,246,6],[246,7,246,9],[246,10,246,13],[246,14,246,17],[247,1,247,2],[247,3,247,6],[247,7,247,9],[247,10,247,13],[247,14,247,17]],"merged_total":5443,"flags":["merged_cut"]}
[{"$nulls":8},"气动切断阀（2、3、5工序）\nON-OFF AUTOMATIC VALVE( PNEUMATIC)"]
["项目名称\nPROJECT",null,"数智化改造项目-自动化升级改造",null,null,"图号\nDWG.NO.",null,null,"20243701-5-ZK-04-05",{"$nulls":4},"设计\nDES.","崔建峰"]
["用户\nCLIENT",null,"重庆聚狮新材料科技有限公司",null,null,"设计阶段\nSTAGE",null,null,"施工图",null,"版次\nREV.",0,null,"校核\nCHK.","袁华"]
["装置/主项\nDEVICE/SUBJECT",null,"共计：44台",null,null,"专业\nSPECIALTY",null,null,"自控",null,"工程编号\nPNO.",20243701,null,"审核\nAPPD.","李俊民"]
[1,"位号 TAG NO.",{"$nulls":5},"1KV-1（221~521）",null,null,"阀盖形式 Bonnet Type",{"$nulls":3},"供应商填写"]
[2,{"$nulls":9},"允许最大压差 Allow △P Mpa(G)",{"$nulls":3},"供应商填写"]
[3,"数量 Q'ty",{"$nulls":5},5,null,null,"最大开度 Open %AT MAX.Flow",{"$nulls":3},"供应商填写"]
[4,"用途   Service",{"$nulls":5},"1V1（101-501）放料罐冲洗液进口开关阀",null,null,"计算CV  CALC.Cv",{"$nulls":3},"供应商填写"]
[5,{"$nulls":9},"选择CV Selected Cv",{"$nulls":3},"供应商填写"]
[6,"P&ID号 P&ID NO",{"$nulls":5},"20241215-01-GY-03- 04A",null,null,"连接形式 Connection Type",{"$nulls":3},"法兰式"]
[7]
[8,"管道或设备号 LINE ＆ EQUIP.NO.",{"$nulls":5},"1PL-2104-80-C4S-N",null,null,"执行机构 Actuator"]
[9,{"$nulls":9},"型号 Model"]
[10,"流体参数",null,"介质 ",{"$nulls":3},"工艺液体（NMP+NaCl+水 )",null,null,"型式 Type",{"$nulls":3},"单作用活塞式"]
[11,"Fluid data",null,"Fluid",{"$nulls":6},"作用形式 Action Style",{"$nulls":3},"气开"]
[12,null,null,"压力","阀前压力",null,null,0.4,null,null,"弹簧范围 Spring Range"]
[13,null,null,"Press","Upstream Pressure",{"$nulls":5},"行程 Travel"]
[14,{"$nulls":3},"阀后压力",null,null,0.36,null,null,"手轮 Hand Wheel",{"$nulls":3},"YES"]
[15,{"$nulls":3},"Downstream Pressure",{"$nulls":5},"供气压力 Air Supply Press",{"$nulls":3},"400~700kpa"]
[16,{"$nulls":3},"阀关闭压差",null,null,0.4,null,null,"气信号接口尺寸 PNEU.CONN.Size",{"$nulls":3},"1/4\"NPT"]
[17,{"$nulls":3},"Shut-off Diff Pressure"]
[18,{"$nulls":3},"单位 Unit",null,null,"Mpa(G)",null,null,"附件 Accessories"]
[19,null,null,"温度 Temp.","操作Oper.",null,null,60,null,null,"过滤减压阀 Regulator ",{"$nulls":3},"YES"]
[20,null,null,"  (Deg. C)","设计Des.",{"$nulls":5},"限位开关 Limited Switch ",{"$nulls":3},"YES"]
[21,null,null,"密度 Density","操作Oper.",null,null,"1028kg/m3",null,null,"电磁阀 Solenoid valve",{"$nulls":3},"二位三通，低功耗"]
[22,null,null,"流量","最小 Min.",{"$nulls":5},"电源 Power Supply",{"$nulls":3},"24VDC"]
[23,null,null,"Flow rate","正常 Nor.",null,null,12,null,null,"防爆等级 Ex.Certification",{"$nulls":3},"ExdIIBT4"]
[24,{"$nulls":3},"最大 Max.",null,null,14,null,null,"电气接口尺寸 ELEC.CONN.Size",{"$nulls":3},"1/2\"NPT(F)"]
[25,{"$nulls":3},"单位 Unit",null,null,"m3/h",null,null,"保位阀 Locked Valve"]
[26,null,null,"管道规格 Specification",{"$nulls":3},"DN80",null,null,"备用钢瓶 Spare Cylinder"]
[27,null,null,"管道材料 Material",{"$nulls":3},"316L",null,null,"制造厂 Manufacturer"]
[28,null,null,"动力粘度 Viscosity  (CP)",{"$nulls":3},1.65]
[29,null,null,"压缩系数 Compress Factor",{"$nulls":6},"备注 Remarks"]
[30,null,null,"气化压力 Vapor Pressure Mpa",{"$nulls":6},"阀门口径、内件、气源接口尺寸等的选择以最终确定的供货商设计计算选型为准。"]
[31,null,null,"临界压力 Critical Press Mpa"]
[32,null,null,"噪音 Noise Level",{"$nulls":6},"带符合工艺及仪表要求的配对法兰，垫片(RPTFE)、紧固件及其它阀内安装附件。"]
[33,null,null,"气源故障阀开/关/保持FC/FO/FL",{"$nulls":3},"FC"]
[34,"阀体/阀芯规格 ",null,"型号 Model"]
[35,"Body/Plug ",null,"阀形式 Valve Style",{"$nulls":3},"球阀"]
[36,"Specification",null,"流开/流关 Flow Open/Close"]
[37,null,null,"阀座数量 Seat NO."]
[38,null,null,"阀芯形式 Plug Type",{"$nulls":3},"浮动O型球"]
[39,null,null,"阀口径 Port size",{"$nulls":3},{"$f":"H30","v":"DN80"}]
[40,null,null,"流量特性 Flow Characteristic",{"$nulls":3},"ON-OFF"]
[41,null,null,"阀体材质 Body Material",{"$nulls":3},"CF3M"]
[42,null,null,"阀芯材质 Plug Material",{"$nulls":3},"316L"]
[43,null,null,"阀座材质 Seat Material",{"$nulls":3},"316L"]
[44,null,null,"阀杆材质 Stem Material",{"$nulls":3},"S20910"]
[45,null,null,"连接尺寸","尺寸  Size",null,null,{"$f":"H43","v":"DN80"}]
[46,null,null,"Process","标准 Rating",null,null,"HG20592-2009(B) PN16 SO-RF"]
[47,null,null,"connection"]
[48,null,null,"法兰材质 Flange Material",{"$nulls":3},"同阀体"]
[49,null,null,"填料 Packing",{"$nulls":3},"PTFE"]
[50,null,null,"泄漏等级 Leakage Class",{"$nulls":3},"ANSI V"]
[1,"位号 TAG NO.",{"$nulls":5},"1KV-1（222~522）",null,null,"阀盖形式 Bonnet Type",{"$nulls":3},"供应商填写"]
[2,{"$nulls":9},"允许最大压差 Allow △P Mpa(G)",{"$nulls":3},"供应商填写"]
[3,"数量 Q'ty",{"$nulls":5},5,null,null,"最大开度 Open %AT MAX.Flow",{"$nulls":3},"供应商填写"]
[4,"用途   Service",{"$nulls":5},"1V1（101~501）放料罐底部氮气进口开关阀",null,null,"计算CV  CALC.Cv",{"$nulls":3},"供应商填写"]
[5,{"$nulls":9},"选择CV Selected Cv",{"$nulls":3},"供应商填写"]
[6,"P&ID号 P&ID NO",{"$nulls":5},"20241215-01-GY-03- 04A",null,null,"连接形式 Connection Type",{"$nulls":3},"法兰式"]
[7]
[8,"管道或设备号 LINE ＆ EQUIP.NO.",{"$nulls":5},"1N-1144-25-C1S-N",null,null,"执行机构 Actuator"]
[9,{"$nulls":9},"型号 Model"]
[10,"流体参数",null,"介质 ",{"$nulls":3},"氮气",null,null,"型式 Type",{"$nulls":3},"单作用活塞式"]
[11,"Fluid data",null,"Fluid",{"$nulls":6},"作用形式 Action Style",{"$nulls":3},"气开"]
[12,null,null,"压力","阀前压力",null,null,0.4,null,null,"弹簧范围 Spring Range"]
[13,null,null,"Press","Upstream Pressure",{"$nulls":5},"行程 Travel"]
[14,{"$nulls":3},"阀后压力",null,null,0.36,null,null,"手轮 Hand Wheel",{"$nulls":3},"YES"]
[15,{"$nulls":3},"Downstream Pressure",{"$nulls":5},"供气压力 Air Supply Press",{"$nulls":3},"400~700kpa"]
[16,{"$nulls":3},"阀关闭压差",null,null,0.4,null,null,"气信号接口尺寸 PNEU.CONN.Size",{"$nulls":3},"1/4\"NPT"]
[17,{"$nulls":3},"Shut-off Diff Pressure"]
[18,{"$nulls":3},"单位 Unit",null,null,"Mpa(G)",null,null,"附件 Accessories"]
[19,null,null,"温度 Temp.","操作Oper.",null,null,"常温",null,null,"过滤减压阀 Regulator ",{"$nulls":3},"YES"]
[20,null,null,"  (Deg. C)","设计Des.",{"$nulls":5},"限位开关 Limited Switch ",{"$nulls":3},"YES"]
[21,null,null,"密度 Density","操作Oper.",null,null,"1.24kg/m3（标）",null,null,"电磁阀 Solenoid valve",{"$nulls":3},"二位三通，低功耗"]
[22,null,null,"流量","最小 Min.",{"$nulls":5},"电源 Power Supply",{"$nulls":3},"24VDC"]
[23,null,null,"Flow rate","正常 Nor.",{"$nulls":5},"防爆等级 Ex.Certification",{"$nulls":3},"ExdIIBT4"]
[24,{"$nulls":3},"最大 Max.",{"$nulls":5},"电气接口尺寸 ELEC.CONN.Size",{"$nulls":3},"1/2\"NPT(F)"]
[25,{"$nulls":3},"单位 Unit",null,null,"m3/h",null,null,"保位阀 Locked Valve"]
[26,null,null,"管道规格 Specification",{"$nulls":3},"DN25",null,null,"备用钢瓶 Spare Cylinder"]
[27,null,null,"管道材料 Material",{"$nulls":3},"316L",null,null,"制造厂 Manufacturer"]
[28,null,null,"动力粘度 Viscosity  (CP)",{"$nulls":3},1]
[29,null,null,"压缩系数 Compress Factor",{"$nulls":6},"备注 Remarks"]
[30,null,null,"气化压力 Vapor Pressure Mpa",{"$nulls":6},"阀门口径、内件、气源接口尺寸等的选择以最终确定的供货商设计计算选型为准。"]
[31,null,null,"临界压力 Critical Press Mpa"]
[32,null,null,"噪音 Noise Level",{"$nulls":6},"带符合工艺及仪表要求的配对法兰，垫片(RPTFE)、紧固件及其它阀内安装附件。"]
[33,null,null,"气源故障阀开/关/保持FC/FO/FL",{"$nulls":3},"FC"]
[34,"阀体/阀芯规格 ",null,"型号 Model"]
[35,"Body/Plug ",null,"阀形式 Valve Style",{"$nulls":3},"球阀"]
[36,"Specification",null,"流开/流关 Flow Open/Close"]
[37,null,null,"阀座数量 Seat NO."]
[38,null,null,"阀芯形式 Plug Type",{"$nulls":3},"浮动O型球"]
[39,null,null,"阀口径 Port size",{"$nulls":3},{"$f":"H80","v":"DN25"}]
[40,null,null,"流量特性 Flow Characteristic",{"$nulls":3},"ON-OFF"]
[41,null,null,"阀体材质 Body Material",{"$nulls":3},"CF3M"]
[42,null,null,"阀芯材质 Plug Material",{"$nulls":3},"316L"]
[43,null,null,"阀座材质 Seat Material",{"$nulls":3},"316L"]
[44,null,null,"阀杆材质 Stem Material",{"$nulls":3},630]
[45,null,null,"连接尺寸","尺寸  Size",null,null,{"$f":"H93","v":"DN25"}]
[46,null,null,"Process","标准 Rating",null,null,"HG20592-2009(B) PN16 SO-RF"]
[47,null,null,"connection"]
[48,null,null,"法兰材质 Flange Material",{"$nulls":3},"同阀体"]
[49,null,null,"填料 Packing",{"$nulls":3},"PTFE"]
[50,null,null,"泄漏等级 Leakage Class",{"$nulls":3},"ANSI V"]
[1,"位号 TAG NO.",{"$nulls":5},"1KV-1523",null,null,"阀盖形式 Bonnet Type",{"$nulls":3},"供应商填写"]
[2,{"$nulls":9},"允许最大压差 Allow △P Mpa(G)",{"$nulls":3},"供应商填写"]
[3,"数量 Q'ty",{"$nulls":5},1,null,null,"最大开度 Open %AT MAX.Flow",{"$nulls":3},"供应商填写"]
[4,"用途   Service",{"$nulls":5},"1V1501放料罐放空开关阀",null,null,"计算CV  CALC.Cv",{"$nulls":3},"供应商填写"]
[5,{"$nulls":9},"选择CV Selected Cv",{"$nulls":3},"供应商填写"]
[6,"P&ID号 P&ID NO",{"$nulls":5},"20241215-01-GY-03- 04E",null,null,"连接形式 Connection Type",{"$nulls":3},"法兰式"]
[7]
[8,"管道或设备号 LINE ＆ EQUIP.NO.",{"$nulls":5},"1VT-2504-80-C4S-N",null,null,"执行机构 Actuator"]
[9,{"$nulls":9},"型号 Model"]
[10,"流体参数",null,"介质 ",{"$nulls":3},"工艺混合气体（氮气+氧气+醋酸）",null,null,"型式 Type",{"$nulls":3},"单作用活塞式"]
[11,"Fluid data",null,"Fluid",{"$nulls":6},"作用形式 Action Style",{"$nulls":3},"气开"]
[12,null,null,"压力","阀前压力",null,null,0.18,null,null,"弹簧范围 Spring Range"]
[13,null,null,"Press","Upstream Pressure",{"$nulls":5},"行程 Travel"]
[14,{"$nulls":3},"阀后压力",null,null,0.18,null,null,"手轮 Hand Wheel",{"$nulls":3},"YES"]
[15,{"$nulls":3},"Downstream Pressure",{"$nulls":5},"供气压力 Air Supply Press",{"$nulls":3},"400~700kpa"]
[16,{"$nulls":3},"阀关闭压差",null,null,0,null,null,"气信号接口尺寸 PNEU.CONN.Size",{"$nulls":3},"1/4\"NPT"]
[17,{"$nulls":3},"Shut-off Diff Pressure"]
[18,{"$nulls":3},"单位 Unit",null,null,"Mpa(G)",null,null,"附件 Accessories"]
[19,null,null,"温度 Temp.","操作Oper.",null,null,120,null,null,"过滤减压阀 Regulator ",{"$nulls":3},"YES"]
[20,null,null,"  (Deg. C)","设计Des.",{"$nulls":5},"限位开关 Limited Switch ",{"$nulls":3},"YES"]
[21,null,null,"密度 Density","操作Oper.",null,null,"1.34kg/m3（标）",null,null,"电磁阀 Solenoid valve",{"$nulls":3},"二位三通，低功耗"]
[22,null,null,"流量","最小 Min.",{"$nulls":5},"电源 Power Supply",{"$nulls":3},"24VDC"]
[23,null,null,"Flow rate","正常 Nor.",null,null,100,null,null,"防爆等级 Ex.Certification",{"$nulls":3},"ExdIIBT4"]
[24,{"$nulls":3},"最大 Max.",{"$nulls":5},"电气接口尺寸 ELEC.CONN.Size",{"$nulls":3},"1/2\"NPT(F)"]
[25,{"$nulls":3},"单位 Unit",null,null,"m3/h",null,null,"保位阀 Locked Valve"]
[26,null,null,"管道规格 Specification",{"$nulls":3},"DN80",null,null,"备用钢瓶 Spare Cylinder"]
[27,null,null,"管道材料 Material",{"$nulls":3},"316L",null,null,"制造厂 Manufacturer"]
[28,null,null,"动力粘度 Viscosity  (CP)"]
[29,null,null,"压缩系数 Compress Factor",{"$nulls":6},"备注 Remarks"]
[30,null,null,"气化压力 Vapor Pressure Mpa",{"$nulls":6},"阀门口径、内件、气源接口尺寸等的选择以最终确定的供货商设计计算选型为准。"]
[31,null,null,"临界压力 Critical Press Mpa"]
[32,null,null,"噪音 Noise Level",{"$nulls":6},"带符合工艺及仪表要求的配对法兰，垫片(RPTFE)、紧固件及其它阀内安装附件。"]
[33,null,null,"气源故障阀开/关/保持FC/FO/FL",{"$nulls":3},"FO"]
[34,"阀体/阀芯规格 ",null,"型号 Model"]
[35,"Body/Plug ",null,"阀形式 Valve Style",{"$nulls":3},"球阀"]
[36,"Specification",null,"流开/流关 Flow Open/Close"]
[37,null,null,"阀座数量 Seat NO."]
[38,null,null,"阀芯形式 Plug Type",{"$nulls":3},"浮动O型球"]
[39,null,null,"阀口径 Port size",{"$nulls":3},{"$f":"H130","v":"DN80"}]
[40,null,null,"流量特性 Flow Characteristic",{"$nulls":3},"ON-OFF"]
[41,null,null,"阀体材质 Body Material",{"$nulls":3},"CF3M"]
[42,null,null,"阀芯材质 Plug Material",{"$nulls":3},"316L"]
[43,null,null,"阀座材质 Seat Material",{"$nulls":3},"316L"]
[44,null,null,"阀杆材质 Stem Material",{"$nulls":3},"S20910"]
[45,null,null,"连接尺寸","尺寸  Size",null,null,{"$f":"H143","v":"DN80"}]
[46,null,null,"Process","标准 Rating",null,null,"HG20592-2009(B) PN16 SO-RF"]
[47,null,null,"connection"]
[48,null,null,"法兰材质 Flange Material",{"$nulls":3},"同阀体"]
[49,null,null,"填料 Packing",{"$nulls":3},"PTFE"]
[50,null,null,"泄漏等级 Leakage Class",{"$nulls":3},"ANSI V"]
[1,"位号 TAG NO.",{"$nulls":5},"1KV-1524",null,null,"阀盖形式 Bonnet Type",{"$nulls":3},"供应商填写"]
[2,{"$nulls":9},"允许最大压差 Allow △P Mpa(G)",{"$nulls":3},"供应商填写"]
[3,"数量 Q'ty",{"$nulls":5},1,null,null,"最大开度 Open %AT MAX.Flow",{"$nulls":3},"供应商填写"]
[4,"用途   Service",{"$nulls":5},"1V1501放料罐氮气进口开关阀",null,null,"计算CV  CALC.Cv",{"$nulls":3},"供应商填写"]
[5,{"$nulls":9},"选择CV Selected Cv",{"$nulls":3},"供应商填写"]
[6,"P&ID号 P&ID NO",{"$nulls":5},"20241215-01-GY-03- 04E",null,null,"连接形式 Connection Type",{"$nulls":3},"法兰式"]
[7]
[8,"管道或设备号 LINE ＆ EQUIP.NO.",{"$nulls":5},"1N1-1507-25-C1S-N",null,null,"执行机构 Actuator"]
[9,{"$nulls":9},"型号 Model"]
[10,"流体参数",null,"介质 ",{"$nulls":3},"氮气",null,null,"型式 Type",{"$nulls":3},"单作用活塞式"]
[11,"Fluid data",null,"Fluid",{"$nulls":6},"作用形式 Action Style",{"$nulls":3},"气开"]
[12,null,null,"压力","阀前压力",null,null,0.4,null,null,"弹簧范围 Spring Range"]
[13,null,null,"Press","Upstream Pressure",{"$nulls":5},"行程 Travel"]
[14,{"$nulls":3},"阀后压力",null,null,0.36,null,null,"手轮 Hand Wheel",{"$nulls":3},"YES"]
[15,{"$nulls":3},"Downstream Pressure",{"$nulls":5},"供气压力 Air Supply Press",{"$nulls":3},"400~700kpa"]
[16,{"$nulls":3},"阀关闭压差",null,null,0.4,null,null,"气信号接口尺寸 PNEU.CONN.Size",{"$nulls":3},"1/4\"NPT"]
[17,{"$nulls":3},"Shut-off Diff Pressure"]
[18,{"$nulls":3},"单位 Unit",null,null,"Mpa(G)",null,null,"附件 Accessories"]
[19,null,null,"温度 Temp.","操作Oper.",null,null,"常温",null,null,"过滤减压阀 Regulator ",{"$nulls":3},"YES"]
[20,null,null,"  (Deg. C)","设计Des.",{"$nulls":5},"限位开关 Limited Switch ",{"$nulls":3},"YES"]
[21,null,null,"密度 Density","操作Oper.",null,null,"1.24kg/m3（标）",null,null,"电磁阀 Solenoid valve",{"$nulls":3},"二位三通，低功耗"]
[22,null,null,"流量","最小 Min.",{"$nulls":5},"电源 Power Supply",{"$nulls":3},"24VDC"]
[23,null,null,"Flow rate","正常 Nor.",{"$nulls":5},"防爆等级 Ex.Certification",{"$nulls":3},"ExdIIBT4"]
[24,{"$nulls":3},"最大 Max.",{"$nulls":5},"电气接口尺寸 ELEC.CONN.Size",{"$nulls":3},"1/2\"NPT(F)"]
[25,{"$nulls":3},"单位 Unit",null,null,"m3/h",null,null,"保位阀 Locked Valve"]
[26,null,null,"管道规格 Specification",{"$nulls":3},"DN25",null,null,"备用钢瓶 Spare Cylinder"]
[27,null,null,"管道材料 Material",{"$nulls":3},"316L",null,null,"制造厂 Manufacturer"]
[28,null,null,"动力粘度 Viscosity  (CP)",{"$nulls":3},1]
[29,null,null,"压缩系数 Compress Factor",{"$nulls":6},"备注 Remarks"]
[30,null,null,"气化压力 Vapor Pressure Mpa",{"$nulls":6},"阀门口径、内件、气源接口尺寸等的选择以最终确定的供货商设计计算选型为准。"]
[31,null,null,"临界压力 Critical Press Mpa"]
[32,null,null,"噪音 Noise Level",{"$nulls":6},"带符合工艺及仪表要求的配对法兰，垫片(RPTFE)、紧固件及其它阀内安装附件。"]
[33,null,null,"气源故障阀开/关/保持FC/FO/FL",{"$nulls":3},"FC"]
[34,"阀体/阀芯规格 ",null,"型号 Model"]
[35,"Body/Plug ",null,"阀形式 Valve Style",{"$nulls":3},"球阀"]
[36,"Specification",null,"流开/流关 Flow Open/Close"]
[37,null,null,"阀座数量 Seat NO."]
[38,null,null,"阀芯形式 Plug Type",{"$nulls":3},"浮动O型球"]
[39,null,null,"阀口径 Port size",{"$nulls":3},{"$f":"H180","v":"DN25"}]
[40,null,null,"流量特性 Flow Characteristic",{"$nulls":3},"ON-OFF"]
[41,null,null,"阀体材质 Body Material",{"$nulls":3},"CF3M"]
[42,null,null,"阀芯材质 Plug Material",{"$nulls":3},"316L"]
[43,null,null,"阀座材质 Seat Material",{"$nulls":3},"316L"]
[44,null,null,"阀杆材质 Stem Material",{"$nulls":3},630]
[45,null,null,"连接尺寸","尺寸  Size",null,null,{"$f":"H193","v":"DN25"}]
[46,null,null,"Process","标准 Rating",null,null,"HG20592-2009(B) PN16 SO-RF"]
[47,null,null,"connection"]
[48,null,null,"法兰材质 Flange Material",{"$nulls":3},"同阀体"]
[49,null,null,"填料 Packing",{"$nulls":3},"PTFE"]
[50,null,null,"泄漏等级 Leakage Class",{"$nulls":3},"ANSI V"]
[1,"位号 TAG NO.",{"$nulls":5},"1KV-2（103-503）",null,null,"阀盖形式 Bonnet Type",{"$nulls":3},"供应商填写"]
[2,{"$nulls":9},"允许最大压差 Allow △P Mpa(G)",{"$nulls":3},"供应商填写"]
[3,"数量 Q'ty",{"$nulls":5},5,null,null,"最大开度 Open %AT MAX.Flow",{"$nulls":3},"供应商填写"]
[4,"用途   Service",{"$nulls":5},"1V2（103-503）半成品配浆槽出口开关阀 ",null,null,"计算CV  CALC.Cv",{"$nulls":3},"供应商填写"]
[5,{"$nulls":9},"选择CV Selected Cv",{"$nulls":3},"供应商填写"]
[6,"P&ID号 P&ID NO",{"$nulls":5},"20241215-02-GY-03- 02A",null,null,"连接形式 Connection Type",{"$nulls":3},"法兰式"]
[7]
[8,"管道或设备号 LINE ＆ EQUIP.NO.",{"$nulls":5},"1PLS-2101-150-C2S-N",null,null,"执行机构 Actuator"]
[9,{"$nulls":9},"型号 Model"]
[10,"流体参数",null,"介质 ",{"$nulls":3},"工艺固液混合物(PPS+水 )",null,null,"型式 Type",{"$nulls":3},"单作用活塞式"]
[11,"Fluid data",null,"Fluid",{"$nulls":6},"作用形式 Action Style",{"$nulls":3},"气开"]
[12,null,null,"压力","阀前压力",null,null,0.02,null,null,"弹簧范围 Spring Range"]
[13,null,null,"Press","Upstream Pressure",{"$nulls":5},"行程 Travel"]
[14,{"$nulls":3},"阀后压力",null,null,0.01,null,null,"手轮 Hand Wheel",{"$nulls":3},"YES"]
[15,{"$nulls":3},"Downstream Pressure",{"$nulls":5},"供气压力 Air Supply Press",{"$nulls":3},"400~700kpa"]
[16,{"$nulls":3},"阀关闭压差",null,null,0.02,null,null,"气信号接口尺寸 PNEU.CONN.Size",{"$nulls":3},"1/4\"NPT"]
[17,{"$nulls":3},"Shut-off Diff Pressure"]
[18,{"$nulls":3},"单位 Unit",null,null,"Mpa(G)",null,null,"附件 Accessories"]
[19,null,null,"温度 Temp.","操作Oper.",null,null,30,null,null,"过滤减压阀 Regulator ",{"$nulls":3},"YES"]
[20,null,null,"  (Deg. C)","设计Des.",{"$nulls":5},"限位开关 Limited Switch ",{"$nulls":3},"YES"]
[21,null,null,"密度 Density","操作Oper.",null,null,"1040kg/m3",null,null,"电磁阀 Solenoid valve",{"$nulls":3},"二位三通，低功耗"]
[22,null,null,"流量","最小 Min.",{"$nulls":5},"电源 Power Supply",{"$nulls":3},"24VDC"]
[23,null,null,"Flow rate","正常 Nor.",null,null,60,null,null,"防爆等级 Ex.Certification",{"$nulls":3},"ExdIIBT4"]
[24,{"$nulls":3},"最大 Max.",{"$nulls":5},"电气接口尺寸 ELEC.CONN.Size",{"$nulls":3},"1/2\"NPT(F)"]
[25,{"$nulls":3},"单位 Unit",null,null,"m3/h",null,null,"保位阀 Locked Valve"]
[26,null,null,"管道规格 Specification",{"$nulls":3},"DN150",null,null,"备用钢瓶 Spare Cylinder"]
[27,null,null,"管道材料 Material",{"$nulls":3},"S30408",null,null,"制造厂 Manufacturer"]
[28,null,null,"动力粘度 Viscosity  (CP)",{"$nulls":3},1.53]
[29,null,null,"压缩系数 Compress Factor",{"$nulls":6},"备注 Remarks"]
[30,null,null,"气化压力 Vapor Pressure Mpa",{"$nulls":6},"阀门口径、内件、气源接口尺寸等的选择以最终确定的供货商设计计算选型为准。"]
[31,null,null,"临界压力 Critical Press Mpa"]
[32,null,null,"噪音 Noise Level",{"$nulls":6},"带符合工艺及仪表要求的配对法兰，垫片(RPTFE)、紧固件及其它阀内安装附件。"]
[33,null,null,"气源故障阀开/关/保持FC/FO/FL",{"$nulls":3},"FC"]
[34,"阀体/阀芯规格 ",null,"型号 Model"]
[35,"Body/Plug ",null,"阀形式 Valve Style",{"$nulls":3},"蝶阀"]
[36,"Specification",null,"流开/流关 Flow Open/Close"]
[37,null,null,"阀座数量 Seat NO."]
[38,null,null,"阀芯形式 Plug Type",{"$nulls":3},"蝶阀"]
[39,null,null,"阀口径 Port size",{"$nulls":3},{"$f":"H230","v":"DN150"}]
[40,null,null,"流量特性 Flow Characteristic",{"$nulls":3},"ON-OFF"]
[41,null,null,"阀体材质 Body Material",{"$nulls":3},"CF8"]
[42,null,null,"阀芯材质 Plug Material",{"$nulls":3},304]
[43,null,null,"阀座材质 Seat Material",{"$nulls":3},304]
[44,null,null,"阀杆材质 Stem Material",{"$nulls":3},630]
[45,null,null,"连接尺寸","尺寸  Size",null,null,{"$f":"H243","v":"DN150"}]
[46,null,null,"Process","标准 Rating",null,null,"HG20592-2009(B) PN16 SO-RF"]
[47,null,null,"connection"]
[48,null,null,"法兰材质 Flange Material",{"$nulls":3},"同阀体"]
[49,null,null,"填料 Packing",{"$nulls":3},"PTFE"]
[50,null,null,"泄漏等级 Leakage Class",{"$nulls":3},"ANSI V"]
[1,"位号 TAG NO.",{"$nulls":5},"1KV-2104",null,null,"阀盖形式 Bonnet Type",{"$nulls":3},"供应商填写"]
[2,{"$nulls":9},"允许最大压差 Allow △P Mpa(G)",{"$nulls":3},"供应商填写"]
[3,"数量 Q'ty",{"$nulls":5},1,null,null,"最大开度 Open %AT MAX.Flow",{"$nulls":3},"供应商填写"]
[4,"用途   Service",{"$nulls":5},"1P2101半成品料浆泵进口冲洗水给水切断",null,null,"计算CV  CALC.Cv",{"$nulls":3},"供应商填写"]
[5,{"$nulls":9},"选择CV Selected Cv",{"$nulls":3},"供应商填写"]
[6,"P&ID号 P&ID NO",{"$nulls":5},"20241215-02-GY-03- 02A",null,null,"连接形式 Connection Type",{"$nulls":3},"法兰式"]
[7]
[8,"管道或设备号 LINE ＆ EQUIP.NO.",{"$nulls":5},"1DW-2103-25-C2S-N",null,null,"执行机构 Actuator"]
[9,{"$nulls":9},"型号 Model"]
[10,"流体参数",null,"介质 ",{"$nulls":3},"脱盐水",null,null,"型式 Type",{"$nulls":3},"单作用活塞式"]
[11,"Fluid data",null,"Fluid",{"$nulls":6},"作用形式 Action Style",{"$nulls":3},"气开"]
[12,null,null,"压力","阀前压力",null,null,0.4,null,null,"弹簧范围 Spring Range"]
[13,null,null,"Press","Upstream Pressure",{"$nulls":5},"行程 Travel"]
[14,{"$nulls":3},"阀后压力",null,null,0.36,null,null,"手轮 Hand Wheel",{"$nulls":3},"YES"]
[15,{"$nulls":3},"Downstream Pressure",{"$nulls":5},"供气压力 Air Supply Press",{"$nulls":3},"400~700kpa"]
[16,{"$nulls":3},"阀关闭压差",null,null,0.4,null,null,"气信号接口尺寸 PNEU.CONN.Size",{"$nulls":3},"1/4\"NPT"]
[17,{"$nulls":3},"Shut-off Diff Pressure"]
[18,{"$nulls":3},"单位 Unit",null,null,"Mpa(G)",null,null,"附件 Accessories"]
[19,null,null,"温度 Temp.","操作Oper.",null,null,"常温",null,null,"过滤减压阀 Regulator ",{"$nulls":3},"YES"]
[20,null,null,"  (Deg. C)","设计Des.",{"$nulls":5},"限位开关 Limited Switch ",{"$nulls":3},"YES"]
[21,null,null,"密度 Density","操作Oper.",null,null,"1000kg/m3",null,null,"电磁阀 Solenoid valve",{"$nulls":3},"二位三通，低功耗"]
[22,null,null,"流量","最小 Min.",null,null,1,null,null,"电源 Power Supply",{"$nulls":3},"24VDC"]
[23,null,null,"Flow rate","正常 Nor.",null,null,2,null,null,"防爆等级 Ex.Certification",{"$nulls":3},"ExdIIBT4"]
[24,{"$nulls":3},"最大 Max.",null,null,3.5,null,null,"电气接口尺寸 ELEC.CONN.Size",{"$nulls":3},"1/2\"NPT(F)"]
[25,{"$nulls":3},"单位 Unit",null,null,"m3/h",null,null,"保位阀 Locked Valve"]
[26,null,null,"管道规格 Specification",{"$nulls":3},"DN25",null,null,"备用钢瓶 Spare Cylinder"]
[27,null,null,"管道材料 Material",{"$nulls":3},"S30408",null,null,"制造厂 Manufacturer"]
[28,null,null,"动力粘度 Viscosity  (CP)",{"$nulls":3},0.84]
[29,null,null,"压缩系数 Compress Factor",{"$nulls":6},"备注 Remarks"]
[30,null,null,"气化压力 Vapor Pressure Mpa",{"$nulls":6},"阀门口径、内件、气源接口尺寸等的选择以最终确定的供货商设计计算选型为准。"]
[31,null,null,"临界压力 Critical Press Mpa"]
[32,null,null,"噪音 Noise Level",{"$nulls":6},"带符合工艺及仪表要求的配对法兰，垫片(RPTFE)、紧固件及其它阀内安装附件。"]
[33,null,null,"气源故障阀开/关/保持FC/FO/FL",{"$nulls":3},"FC"]
[34,"阀体/阀芯规格 ",null,"型号 Model"]
[35,"Body/Plug ",null,"阀形式 Valve Style",{"$nulls":3},"球阀"]
[36,"Specification",null,"流开/流关 Flow Open/Close"]
[37,null,null,"阀座数量 Seat NO."]
[38,null,null,"阀芯形式 Plug Type",{"$nulls":3},"浮动O型球"]
[39,null,null,"阀口径 Port size",{"$nulls":3},{"$f":"H280","v":"DN25"}]
[40,null,null,"流量特性 Flow Characteristic",{"$nulls":3},"ON-OFF"]
[41,null,null,"阀体材质 Body Material",{"$nulls":3},"CF8"]
[42,null,null,"阀芯材质 Plug Material",{"$nulls":3},304]
[43,null,null,"阀座材质 Seat Material",{"$nulls":3},304]
[44,null,null,"阀杆材质 Stem Material",{"$nulls":3},630]
[45,null,null,"连接尺寸","尺寸  Size",null,null,{"$f":"H293","v":"DN25"}]
[46,null,null,"Process","标准 Rating",null,null,"HG20592-2009(B) PN16 SO-RF"]
[47,null,null,"connection"]
[48,null,null,"法兰材质 Flange Material",{"$nulls":3},"同阀体"]
[49,null,null,"填料 Packing",{"$nulls":3},"PTFE"]
[50,null,null,"泄漏等级 Leakage Class",{"$nulls":3},"ANSI V"]
[1,"位号 TAG NO.",{"$nulls":5},"1KV-2504",null,null,"阀盖形式 Bonnet Type",{"$nulls":3},"供应商填写"]
[2,{"$nulls":9},"允许最大压差 Allow △P Mpa(G)",{"$nulls":3},"供应商填写"]
[3,"数量 Q'ty",{"$nulls":5},1,null,null,"最大开度 Open %AT MAX.Flow",{"$nulls":3},"供应商填写"]
[4,"用途   Service",{"$nulls":5},"1P2501半成品料浆泵进口冲洗水给水切断",null,null,"计算CV  CALC.Cv",{"$nulls":3},"供应商填写"]
[5,{"$nulls":9},"选择CV Selected Cv",{"$nulls":3},"供应商填写"]
[6,"P&ID号 P&ID NO",{"$nulls":5},"20241215-02-GY-03- 02E",null,null,"连接形式 Connection Type",{"$nulls":3},"法兰式"]
[7]
[8,"管道或设备号 LINE ＆ EQUIP.NO.",{"$nulls":5},"1DW-2503-25-C2S-N",null,null,"执行机构 Actuator"]
[9,{"$nulls":9},"型号 Model"]
[10,"流体参数",null,"介质 ",{"$nulls":3},"脱盐水",null,null,"型式 Type",{"$nulls":3},"单作用活塞式"]
[11,"Fluid data",null,"Fluid",{"$nulls":6},"作用形式 Action Style",{"$nulls":3},"气开"]
[12,null,null,"压力","阀前压力",null,null,0.4,null,null,"弹簧范围 Spring Range"]
[13,null,null,"Press","Upstream Pressure",{"$nulls":5},"行程 Travel"]
[14,{"$nulls":3},"阀后压力",null,null,0.36,null,null,"手轮 Hand Wheel",{"$nulls":3},"YES"]
[15,{"$nulls":3},"Downstream Pressure",{"$nulls":5},"供气压力 Air Supply Press",{"$nulls":3},"400~700kpa"]
[16,{"$nulls":3},"阀关闭压差",null,null,0.4,null,null,"气信号接口尺寸 PNEU.CONN.Size",{"$nulls":3},"1/4\"NPT"]
[17,{"$nulls":3},"Shut-off Diff Pressure"]
[18,{"$nulls":3},"单位 Unit",null,null,"Mpa(G)",null,null,"附件 Accessories"]
[19,null,null,"温度 Temp.","操作Oper.",null,null,"常温",null,null,"过滤减压阀 Regulator ",{"$nulls":3},"YES"]
[20,null,null,"  (Deg. C)","设计Des.",{"$nulls":5},"限位开关 Limited Switch ",{"$nulls":3},"YES"]
[21,null,null,"密度 Density","操作Oper.",null,null,"1000kg/m3",null,null,"电磁阀 Solenoid valve",{"$nulls":3},"二位三通，低功耗"]
[22,null,null,"流量","最小 Min.",null,null,1,null,null,"电源 Power Supply",{"$nulls":3},"24VDC"]
[23,null,null,"Flow rate","正常 Nor.",null,null,2,null,null,"防爆等级 Ex.Certification",{"$nulls":3},"ExdIIBT4"]
[24,{"$nulls":3},"最大 Max.",null,null,3.5,null,null,"电气接口尺寸 ELEC.CONN.Size",{"$nulls":3},"1/2\"NPT(F)"]
[25,{"$nulls":3},"单位 Unit",null,null,"m3/h",null,null,"保位阀 Locked Valve"]
[26,null,null,"管道规格 Specification",{"$nulls":3},"DN25",null,null,"备用钢瓶 Spare Cylinder"]
[27,null,null,"管道材料 Material",{"$nulls":3},"S30408",null,null,"制造厂 Manufacturer"]
[28,null,null,"动力粘度 Viscosity  (CP)",{"$nulls":3},0.84]
[29,null,null,"压缩系数 Compress Factor",{"$nulls":6},"备注 Remarks"]
[30,null,null,"气化压力 Vapor Pressure Mpa",{"$nulls":6},"阀门口径、内件、气源接口尺寸等的选择以最终确定的供货商设计计算选型为准。"]
[31,null,null,"临界压力 Critical Press Mpa"]
[32,null,null,"噪音 Noise Level",{"$nulls":6},"带符合工艺及仪表要求的配对法兰，垫片(RPTFE)、紧固件及其它阀内安装附件。"]
[33,null,null,"气源故障阀开/关/保持FC/FO/FL",{"$nulls":3},"FC"]
[34,"阀体/阀芯规格 ",null,"型号 Model"]
[35,"Body/Plug ",null,"阀形式 Valve Style",{"$nulls":3},"球阀"]
[36,"Specification",null,"流开/流关 Flow Open/Close"]
[37,null,null,"阀座数量 Seat NO."]
[38,null,null,"阀芯形式 Plug Type",{"$nulls":3},"浮动O型球"]
[39,null,null,"阀口径 Port size",{"$nulls":3},{"$f":"H330","v":"DN25"}]
[40,null,null,"流量特性 Flow Characteristic",{"$nulls":3},"ON-OFF"]
[41,null,null,"阀体材质 Body Material",{"$nulls":3},"CF8"]
[42,null,null,"阀芯材质 Plug Material",{"$nulls":3},304]
[43,null,null,"阀座材质 Seat Material",{"$nulls":3},304]
[44,null,null,"阀杆材质 Stem Material",{"$nulls":3},630]
[45,null,null,"连接尺寸","尺寸  Size",null,null,{"$f":"H343","v":"DN25"}]
[46,null,null,"Process","标准 Rating",null,null,"HG20592-2009(B) PN16 SO-RF"]
[47,null,null,"connection"]
[48,null,null,"法兰材质 Flange Material",{"$nulls":3},"同阀体"]
[49,null,null,"填料 Packing",{"$nulls":3},"PTFE"]
[50,null,null,"泄漏等级 Leakage Class",{"$nulls":3},"ANSI V"]
[1,"位号 TAG NO.",{"$nulls":5},"1KV-2105",null,null,"阀盖形式 Bonnet Type",{"$nulls":3},"供应商填写"]
[2,{"$nulls":9},"允许最大压差 Allow △P Mpa(G)",{"$nulls":3},"供应商填写"]
[3,"数量 Q'ty",{"$nulls":5},1,null,null,"最大开度 Open %AT MAX.Flow",{"$nulls":3},"供应商填写"]
[4,"用途   Service",{"$nulls":5},"1P2101料浆泵出口至1V3001AB混料罐进料开关阀",null,null,"计算CV  CALC.Cv",{"$nulls":3},"供应商填写"]
[5,{"$nulls":9},"选择CV Selected Cv",{"$nulls":3},"供应商填写"]
[6,"P&ID号 P&ID NO",{"$nulls":5},"20241215-02-GY-03- 02A",null,null,"连接形式 Connection Type",{"$nulls":3},"法兰式"]
[7]
[8,"管道或设备号 LINE ＆ EQUIP.NO.",{"$nulls":5},"1PLS-2102-100-C2S-N",null,null,"执行机构 Actuator"]
[9,{"$nulls":9},"型号 Model"]
[10,"流体参数",null,"介质 ",{"$nulls":3},"工艺固液混合物(PPS+水 )",null,null,"型式 Type",{"$nulls":3},"单作用活塞式"]
[11,"Fluid data",null,"Fluid",{"$nulls":6},"作用形式 Action Style",{"$nulls":3},"气开"]
[12,null,null,"压力","阀前压力",null,null,0.4,null,null,"弹簧范围 Spring Range"]
[13,null,null,"Press","Upstream Pressure",{"$nulls":5},"行程 Travel"]
[14,{"$nulls":3},"阀后压力",null,null,0.36,null,null,"手轮 Hand Wheel",{"$nulls":3},"YES"]
[15,{"$nulls":3},"Downstream Pressure",{"$nulls":5},"供气压力 Air Supply Press",{"$nulls":3},"400~700kpa"]
[16,{"$nulls":3},"阀关闭压差",null,null,0.4,null,null,"气信号接口尺寸 PNEU.CONN.Size",{"$nulls":3},"1/4\"NPT"]
[17,{"$nulls":3},"Shut-off Diff Pressure"]
[18,{"$nulls":3},"单位 Unit",null,null,"Mpa(G)",null,null,"附件 Accessories"]
[19,null,null,"温度 Temp.","操作Oper.",null,null,30,null,null,"过滤减压阀 Regulator ",{"$nulls":3},"YES"]
[20,null,null,"  (Deg. C)","设计Des.",{"$nulls":5},"限位开关 Limited Switch ",{"$nulls":3},"YES"]
[21,null,null,"密度 Density","操作Oper.",null,null,"1040kg/m3",null,null,"电磁阀 Solenoid valve",{"$nulls":3},"二位三通，低功耗"]
[22,null,null,"流量","最小 Min.",{"$nulls":5},"电源 Power Supply",{"$nulls":3},"24VDC"]
[23,null,null,"Flow rate","正常 Nor.",null,null,60,null,null,"防爆等级 Ex.Certification",{"$nulls":3},"ExdIIBT4"]
[24,{"$nulls":3},"最大 Max.",{"$nulls":5},"电气接口尺寸 ELEC.CONN.Size",{"$nulls":3},"1/2\"NPT(F)"]
[25,{"$nulls":3},"单位 Unit",null,null,"m3/h",null,null,"保位阀 Locked Valve"]
[26,null,null,"管道规格 Specification",{"$nulls":3},"DN100",null,null,"备用钢瓶 Spare Cylinder"]
[27,null,null,"管道材料 Material",{"$nulls":3},"S30408",null,null,"制造厂 Manufacturer"]
[28,null,null,"动力粘度 Viscosity  (CP)",{"$nulls":3},1.53]
[29,null,null,"压缩系数 Compress Factor",{"$nulls":6},"备注 Remarks"]
[30,null,null,"气化压力 Vapor Pressure Mpa",{"$nulls":6},"阀门口径、内件、气源接口尺寸等的选择以最终确定的供货商设计计算选型为准。"]
[31,null,null,"临界压力 Critical Press Mpa"]
[32,null,null,"噪音 Noise Level",{"$nulls":6},"带符合工艺及仪表要求的配对法兰，垫片(RPTFE)、紧固件及其它阀内安装附件。"]
[33,null,null,"气源故障阀开/关/保持FC/FO/FL",{"$nulls":3},"FL"]
[34,"阀体/阀芯规格 ",null,"型号 Model"]
[35,"Body/Plug ",null,"阀形式 Valve Style",{"$nulls":3},"球阀"]
[36,"Specification",null,"流开/流关 Flow Open/Close"]
[37,null,null,"阀座数量 Seat NO."]
[38,null,null,"阀芯形式 Plug Type",{"$nulls":3},"浮动O型球"]
[39,null,null,"阀口径 Port size",{"$nulls":3},{"$f":"H380","v":"DN100"}]
[40,null,null,"流量特性 Flow Characteristic",{"$nulls":3},"ON-OFF"]
[41,null,null,"阀体材质 Body Material",{"$nulls":3},"CF8"]
[42,null,null,"阀芯材质 Plug Material",{"$nulls":3},304]
[43,null,null,"阀座材质 Seat Material",{"$nulls":3},304]
[44,null,null,"阀杆材质 Stem Material",{"$nulls":3},630]
[45,null,null,"连接尺寸","尺寸  Size",null,null,{"$f":"H393","v":"DN100"}]
[46,null,null,"Process","标准 Rating",null,null,"HG20592-2009(B) PN16 SO-RF"]
[47,null,null,"connection"]
[48,null,null,"法兰材质 Flange Material",{"$nulls":3},"同阀体"]
[49,null,null,"填料 Packing",{"$nulls":3},"PTFE"]
[50,null,null,"泄漏等级 Leakage Class",{"$nulls":3},"ANSI V"]
[1,"位号 TAG NO.",{"$nulls":5},"1KV-2106",null,null,"阀盖形式 Bonnet Type",{"$nulls":3},"供应商填写"]
[2,{"$nulls":9},"允许最大压差 Allow △P Mpa(G)",{"$nulls":3},"供应商填写"]
[3,"数量 Q'ty",{"$nulls":5},1,null,null,"最大开度 Open %AT MAX.Flow",{"$nulls":3},"供应商填写"]
[4,"用途   Service",{"$nulls":5},"1P2101料浆泵出口至1V3102半成品高位槽进料开关阀",null,null,"计算CV  CALC.Cv",{"$nulls":3},"供应商填写"]
[5,{"$nulls":9},"选择CV Selected Cv",{"$nulls":3},"供应商填写"]
[6,"P&ID号 P&ID NO",{"$nulls":5},"20241215-02-GY-03- 02A",null,null,"连接形式 Connection Type",{"$nulls":3},"法兰式"]
[7]
[8,"管道或设备号 LINE ＆ EQUIP.NO.",{"$nulls":5},"1PLS-2103-100-C2S-N",null,null,"执行机构 Actuator"]
[9,{"$nulls":9},"型号 Model"]
[10,"流体参数",null,"介质 ",{"$nulls":3},"工艺固液混合物(PPS+水 )",null,null,"型式 Type",{"$nulls":3},"单作用活塞式"]
[11,"Fluid data",null,"Fluid",{"$nulls":6},"作用形式 Action Style",{"$nulls":3},"气开"]
[12,null,null,"压力","阀前压力",null,null,0.4,null,null,"弹簧范围 Spring Range"]
[13,null,null,"Press","Upstream Pressure",{"$nulls":5},"行程 Travel"]
[14,{"$nulls":3},"阀后压力",null,null,0.36,null,null,"手轮 Hand Wheel",{"$nulls":3},"YES"]
[15,{"$nulls":3},"Downstream Pressure",{"$nulls":5},"供气压力 Air Supply Press",{"$nulls":3},"400~700kpa"]
[16,{"$nulls":3},"阀关闭压差",null,null,0.4,null,null,"气信号接口尺寸 PNEU.CONN.Size",{"$nulls":3},"1/4\"NPT"]
[17,{"$nulls":3},"Shut-off Diff Pressure"]
[18,{"$nulls":3},"单位 Unit",null,null,"Mpa(G)",null,null,"附件 Accessories"]
[19,null,null,"温度 Temp.","操作Oper.",null,null,30,null,null,"过滤减压阀 Regulator ",{"$nulls":3},"YES"]
[20,null,null,"  (Deg. C)","设计Des.",{"$nulls":5},"限位开关 Limited Switch ",{"$nulls":3},"YES"]
[21,null,null,"密度 Density","操作Oper.",null,null,"1040kg/m3",null,null,"电磁阀 Solenoid valve",{"$nulls":3},"二位三通，低功耗"]
[22,null,null,"流量","最小 Min.",{"$nulls":5},"电源 Power Supply",{"$nulls":3},"24VDC"]
[23,null,null,"Flow rate","正常 Nor.",null,null,60,null,null,"防爆等级 Ex.Certification",{"$nulls":3},"ExdIIBT4"]
[24,{"$nulls":3},"最大 Max.",{"$nulls":5},"电气接口尺寸 ELEC.CONN.Size",{"$nulls":3},"1/2\"NPT(F)"]
[25,{"$nulls":3},"单位 Unit",null,null,"m3/h",null,null,"保位阀 Locked Valve"]
[26,null,null,"管道规格 Specification",{"$nulls":3},"DN100",null,null,"备用钢瓶 Spare Cylinder"]
[27,null,null,"管道材料 Material",{"$nulls":3},"S30408",null,null,"制造厂 Manufacturer"]
[28,null,null,"动力粘度 Viscosity  (CP)",{"$nulls":3},1.53]
[29,null,null,"压缩系数 Compress Factor",{"$nulls":6},"备注 Remarks"]
[30,null,null,"气化压力 Vapor Pressure Mpa",{"$nulls":6},"阀门口径、内件、气源接口尺寸等的选择以最终确定的供货商设计计算选型为准。"]
[31,null,null,"临界压力 Critical Press Mpa"]
[32,null,null,"噪音 Noise Level",{"$nulls":6},"带符合工艺及仪表要求的配对法兰，垫片(RPTFE)、紧固件及其它阀内安装附件。"]
[33,null,null,"气源故障阀开/关/保持FC/FO/FL",{"$nulls":3},"FL"]
[34,"阀体/阀芯规格 ",null,"型号 Model"]
[35,"Body/Plug ",null,"阀形式 Valve Style",{"$nulls":3},"球阀"]
[36,"Specification",null,"流开/流关 Flow Open/Close"]
[37,null,null,"阀座数量 Seat NO."]
[38,null,null,"阀芯形式 Plug Type",{"$nulls":3},"浮动O型球"]
[39,null,null,"阀口径 Port size",{"$nulls":3},{"$f":"H430","v":"DN100"}]
[40,null,null,"流量特性 Flow Characteristic",{"$nulls":3},"ON-OFF"]
[41,null,null,"阀体材质 Body Material",{"$nulls":3},"CF8"]
[42,null,null,"阀芯材质 Plug Material",{"$nulls":3},304]
[43,null,null,"阀座材质 Seat Material",{"$nulls":3},304]
[44,null,null,"阀杆材质 Stem Material",{"$nulls":3},630]
[45,null,null,"连接尺寸","尺寸  Size",null,null,{"$f":"H443","v":"DN100"}]
[46,null,null,"Process","标准 Rating",null,null,"HG20592-2009(B) PN16 SO-RF"]
[47,null,null,"connection"]
[48,null,null,"法兰材质 Flange Material",{"$nulls":3},"同阀体"]
[49,null,null,"填料 Packing",{"$nulls":3},"PTFE"]
[50,null,null,"泄漏等级 Leakage Class",{"$nulls":3},"ANSI V"]
[1,"位号 TAG NO.",{"$nulls":5},"1KV-2505",null,null,"阀盖形式 Bonnet Type",{"$nulls":3},"供应商填写"]
[2,{"$nulls":9},"允许最大压差 Allow △P Mpa(G)",{"$nulls":3},"供应商填写"]
[3,"数量 Q'ty",{"$nulls":5},1,null,null,"最大开度 Open %AT MAX.Flow",{"$nulls":3},"供应商填写"]
[4,"用途   Service",{"$nulls":5},"1P2501料浆泵出口至1V3001AB混料罐进料开关阀",null,null,"计算CV  CALC.Cv",{"$nulls":3},"供应商填写"]
[5,{"$nulls":9},"选择CV Selected Cv",{"$nulls":3},"供应商填写"]
[6,"P&ID号 P&ID NO",{"$nulls":5},"20241215-02-GY-03- 02E",null,null,"连接形式 Connection Type",{"$nulls":3},"法兰式"]
[7]
[8,"管道或设备号 LINE ＆ EQUIP.NO.",{"$nulls":5},"1PLS-2502-100-C2S-N",null,null,"执行机构 Actuator"]
[9,{"$nulls":9},"型号 Model"]
[10,"流体参数",null,"介质 ",{"$nulls":3},"工艺固液混合物(PPS+水 )",null,null,"型式 Type",{"$nulls":3},"单作用活塞式"]
[11,"Fluid data",null,"Fluid",{"$nulls":6},"作用形式 Action Style",{"$nulls":3},"气开"]
[12,null,null,"压力","阀前压力",null,null,0.4,null,null,"弹簧范围 Spring Range"]
[13,null,null,"Press","Upstream Pressure",{"$nulls":5},"行程 Travel"]
[14,{"$nulls":3},"阀后压力",null,null,0.36,null,null,"手轮 Hand Wheel",{"$nulls":3},"YES"]
[15,{"$nulls":3},"Downstream Pressure",{"$nulls":5},"供气压力 Air Supply Press",{"$nulls":3},"400~700kpa"]
[16,{"$nulls":3},"阀关闭压差",null,null,0.4,null,null,"气信号接口尺寸 PNEU.CONN.Size",{"$nulls":3},"1/4\"NPT"]
[17,{"$nulls":3},"Shut-off Diff Pressure"]
[18,{"$nulls":3},"单位 Unit",null,null,"Mpa(G)",null,null,"附件 Accessories"]
[19,null,null,"温度 Temp.","操作Oper.",null,null,30,null,null,"过滤减压阀 Regulator ",{"$nulls":3},"YES"]
[20,null,null,"  (Deg. C)","设计Des.",{"$nulls":5},"限位开关 Limited Switch ",{"$nulls":3},"YES"]
[21,null,null,"密度 Density","操作Oper.",null,null,"1040kg/m3",null,null,"电磁阀 Solenoid valve",{"$nulls":3},"二位三通，低功耗"]
[22,null,null,"流量","最小 Min.",{"$nulls":5},"电源 Power Supply",{"$nulls":3},"24VDC"]
[23,null,null,"Flow rate","正常 Nor.",null,null,60,null,null,"防爆等级 Ex.Certification",{"$nulls":3},"ExdIIBT4"]
[24,{"$nulls":3},"最大 Max.",{"$nulls":5},"电气接口尺寸 ELEC.CONN.Size",{"$nulls":3},"1/2\"NPT(F)"]
[25,{"$nulls":3},"单位 Unit",null,null,"m3/h",null,null,"保位阀 Locked Valve"]
[26,null,null,"管道规格 Specification",{"$nulls":3},"DN100",null,null,"备用钢瓶 Spare Cylinder"]
[27,null,null,"管道材料 Material",{"$nulls":3},"S30408",null,null,"制造厂 Manufacturer"]
[28,null,null,"动力粘度 Viscosity  (CP)",{"$nulls":3},1.53]
[29,null,null,"压缩系数 Compress Factor",{"$nulls":6},"备注 Remarks"]
[30,null,null,"气化压力 Vapor Pressure Mpa",{"$nulls":6},"阀门口径、内件、气源接口尺寸等的选择以最终确定的供货商设计计算选型为准。"]
[31,null,null,"临界压力 Critical Press Mpa"]
[32,null,null,"噪音 Noise Level",{"$nulls":6},"带符合工艺及仪表要求的配对法兰，垫片(RPTFE)、紧固件及其它阀内安装附件。"]
[33,null,null,"气源故障阀开/关/保持FC/FO/FL",{"$nulls":3},"FL"]
[34,"阀体/阀芯规格 ",null,"型号 Model"]
[35,"Body/Plug ",null,"阀形式 Valve Style",{"$nulls":3},"球阀"]
[36,"Specification",null,"流开/流关 Flow Open/Close"]
[37,null,null,"阀座数量 Seat NO."]
[38,null,null,"阀芯形式 Plug Type",{"$nulls":3},"浮动O型球"]
[39,null,null,"阀口径 Port size",{"$nulls":3},{"$f":"H480","v":"DN100"}]
[40,null,null,"流量特性 Flow Characteristic",{"$nulls":3},"ON-OFF"]
[41,null,null,"阀体材质 Body Material",{"$nulls":3},"CF8"]
[42,null,null,"阀芯材质 Plug Material",{"$nulls":3},304]
[43,null,null,"阀座材质 Seat Material",{"$nulls":3},304]
[44,null,null,"阀杆材质 Stem Material",{"$nulls":3},630]
[45,null,null,"连接尺寸","尺寸  Size",null,null,{"$f":"H493","v":"DN100"}]
[46,null,null,"Process","标准 Rating",null,null,"HG20592-2009(B) PN16 SO-RF"]
[47,null,null,"connection"]
[48,null,null,"法兰材质 Flange Material",{"$nulls":3},"同阀体"]
[49,null,null,"填料 Packing",{"$nulls":3},"PTFE"]
[50,null,null,"泄漏等级 Leakage Class",{"$nulls":3},"ANSI V"]
[1,"位号 TAG NO.",{"$nulls":5},"1KV-2506",null,null,"阀盖形式 Bonnet Type",{"$nulls":3},"供应商填写"]
[2,{"$nulls":9},"允许最大压差 Allow △P Mpa(G)",{"$nulls":3},"供应商填写"]
[3,"数量 Q'ty",{"$nulls":5},1,null,null,"最大开度 Open %AT MAX.Flow",{"$nulls":3},"供应商填写"]
[4,"用途   Service",{"$nulls":5},"1P2501料浆泵出口至1V3502半成品高位槽进料开关阀",null,null,"计算CV  CALC.Cv",{"$nulls":3},"供应商填写"]
[5,{"$nulls":9},"选择CV Selected Cv",{"$nulls":3},"供应商填写"]
[6,"P&ID号 P&ID NO",{"$nulls":5},"20241215-02-GY-03- 02E",null,null,"连接形式 Connection Type",{"$nulls":3},"法兰式"]
[7]
[8,"管道或设备号 LINE ＆ EQUIP.NO.",{"$nulls":5},"1PLS-2503-100-C2S-N",null,null,"执行机构 Actuator"]
[9,{"$nulls":9},"型号 Model"]
[10,"流体参数",null,"介质 ",{"$nulls":3},"工艺固液混合物(PPS+水 )",null,null,"型式 Type",{"$nulls":3},"单作用活塞式"]
[11,"Fluid data",null,"Fluid",{"$nulls":6},"作用形式 Action Style",{"$nulls":3},"气开"]
[12,null,null,"压力","阀前压力",null,null,0.4,null,null,"弹簧范围 Spring Range"]
[13,null,null,"Press","Upstream Pressure",{"$nulls":5},"行程 Travel"]
[14,{"$nulls":3},"阀后压力",null,null,0.36,null,null,"手轮 Hand Wheel",{"$nulls":3},"YES"]
[15,{"$nulls":3},"Downstream Pressure",{"$nulls":5},"供气压力 Air Supply Press",{"$nulls":3},"400~700kpa"]
[16,{"$nulls":3},"阀关闭压差",null,null,0.4,null,null,"气信号接口尺寸 PNEU.CONN.Size",{"$nulls":3},"1/4\"NPT"]
[17,{"$nulls":3},"Shut-off Diff Pressure"]
[18,{"$nulls":3},"单位 Unit",null,null,"Mpa(G)",null,null,"附件 Accessories"]
[19,null,null,"温度 Temp.","操作Oper.",null,null,30,null,null,"过滤减压阀 Regulator ",{"$nulls":3},"YES"]
[20,null,null,"  (Deg. C)","设计Des.",{"$nulls":5},"限位开关 Limited Switch ",{"$nulls":3},"YES"]
[21,null,null,"密度 Density","操作Oper.",null,null,"1040kg/m3",null,null,"电磁阀 Solenoid valve",{"$nulls":3},"二位三通，低功耗"]
[22,null,null,"流量","最小 Min.",{"$nulls":5},"电源 Power Supply",{"$nulls":3},"24VDC"]
[23,null,null,"Flow rate","正常 Nor.",null,null,60,null,null,"防爆等级 Ex.Certification",{"$nulls":3},"ExdIIBT4"]
[24,{"$nulls":3},"最大 Max.",{"$nulls":5},"电气接口尺寸 ELEC.CONN.Size",{"$nulls":3},"1/2\"NPT(F)"]
[25,{"$nulls":3},"单位 Unit",null,null,"m3/h",null,null,"保位阀 Locked Valve"]
[26,null,null,"管道规格 Specification",{"$nulls":3},"DN100",null,null,"备用钢瓶 Spare Cylinder"]
[27,null,null,"管道材料 Material",{"$nulls":3},"S30408",null,null,"制造厂 Manufacturer"]
[28,null,null,"动力粘度 Viscosity  (CP)",{"$nulls":3},1.53]
[29,null,null,"压缩系数 Compress Factor",{"$nulls":6},"备注 Remarks"]
[30,null,null,"气化压力 Vapor Pressure Mpa",{"$nulls":6},"阀门口径、内件、气源接口尺寸等的选择以最终确定的供货商设计计算选型为准。"]
[31,null,null,"临界压力 Critical Press Mpa"]
[32,null,null,"噪音 Noise Level",{"$nulls":6},"带符合工艺及仪表要求的配对法兰，垫片(RPTFE)、紧固件及其它阀内安装附件。"]
[33,null,null,"气源故障阀开/关/保持FC/FO/FL",{"$nulls":3},"FL"]
[34,"阀体/阀芯规格 ",null,"型号 Model"]
[35,"Body/Plug ",null,"阀形式 Valve Style",{"$nulls":3},"球阀"]
[36,"Specification",null,"流开/流关 Flow Open/Close"]
[37,null,null,"阀座数量 Seat NO."]
[38,null,null,"阀芯形式 Plug Type",{"$nulls":3},"浮动O型球"]
[39,null,null,"阀口径 Port size",{"$nulls":3},{"$f":"H530","v":"DN100"}]
[40,null,null,"流量特性 Flow Characteristic",{"$nulls":3},"ON-OFF"]
[41,null,null,"阀体材质 Body Material",{"$nulls":3},"CF8"]
[42,null,null,"阀芯材质 Plug Material",{"$nulls":3},304]
[43,null,null,"阀座材质 Seat Material",{"$nulls":3},304]
[44,null,null,"阀杆材质 Stem Material",{"$nulls":3},630]
[45,null,null,"连接尺寸","尺寸  Size",null,null,{"$f":"H543","v":"DN100"}]
[46,null,null,"Process","标准 Rating",null,null,"HG20592-2009(B) PN16 SO-RF"]
[47,null,null,"connection"]
[48,null,null,"法兰材质 Flange Material",{"$nulls":3},"同阀体"]
[49,null,null,"填料 Packing",{"$nulls":3},"PTFE"]
[50,null,null,"泄漏等级 Leakage Class",{"$nulls":3},"ANSI V"]
[1,"位号 TAG NO.",{"$nulls":5},"1KV-2（204-404）",null,null,"阀盖形式 Bonnet Type",{"$nulls":3},"供应商填写"]
[2,{"$nulls":9},"允许最大压差 Allow △P Mpa(G)",{"$nulls":3},"供应商填写"]
[3,"数量 Q'ty",{"$nulls":5},3,null,null,"最大开度 Open %AT MAX.Flow",{"$nulls":3},"供应商填写"]
[4,"用途   Service",{"$nulls":5},"1P2（201-401）料浆泵出口至1V3001AB混料罐进料开关阀",null,null,"计算CV  CALC.Cv",{"$nulls":3},"供应商填写"]
[5,{"$nulls":9},"选择CV Selected Cv",{"$nulls":3},"供应商填写"]
[6,"P&ID号 P&ID NO",{"$nulls":5},"20241215-02-GY-03- 02B",null,null,"连接形式 Connection Type",{"$nulls":3},"法兰式"]
[7]
[8,"管道或设备号 LINE ＆ EQUIP.NO.",{"$nulls":5},"1PLS-2202-100-C2S-N",null,null,"执行机构 Actuator"]
[9,{"$nulls":9},"型号 Model"]
[10,"流体参数",null,"介质 ",{"$nulls":3},"工艺固液混合物(PPS+水 )",null,null,"型式 Type",{"$nulls":3},"单作用活塞式"]
[11,"Fluid data",null,"Fluid",{"$nulls":6},"作用形式 Action Style",{"$nulls":3},"气开"]
[12,null,null,"压力","阀前压力",null,null,0.4,null,null,"弹簧范围 Spring Range"]
[13,null,null,"Press","Upstream Pressure",{"$nulls":5},"行程 Travel"]
[14,{"$nulls":3},"阀后压力",null,null,0.36,null,null,"手轮 Hand Wheel",{"$nulls":3},"YES"]
[15,{"$nulls":3},"Downstream Pressure",{"$nulls":5},"供气压力 Air Supply Press",{"$nulls":3},"400~700kpa"]
[16,{"$nulls":3},"阀关闭压差",null,null,0.4,null,null,"气信号接口尺寸 PNEU.CONN.Size",{"$nulls":3},"1/4\"NPT"]
[17,{"$nulls":3},"Shut-off Diff Pressure"]
[18,{"$nulls":3},"单位 Unit",null,null,"Mpa(G)",null,null,"附件 Accessories"]
[19,null,null,"温度 Temp.","操作Oper.",null,null,30,null,null,"过滤减压阀 Regulator ",{"$nulls":3},"YES"]
[20,null,null,"  (Deg. C)","设计Des.",{"$nulls":5},"限位开关 Limited Switch ",{"$nulls":3},"YES"]
[21,null,null,"密度 Density","操作Oper.",null,null,"1040kg/m3",null,null,"电磁阀 Solenoid valve",{"$nulls":3},"二位三通，低功耗"]
[22,null,null,"流量","最小 Min.",{"$nulls":5},"电源 Power Supply",{"$nulls":3},"24VDC"]
[23,null,null,"Flow rate","正常 Nor.",null,null,60,null,null,"防爆等级 Ex.Certification",{"$nulls":3},"ExdIIBT4"]
[24,{"$nulls":3},"最大 Max.",{"$nulls":5},"电气接口尺寸 ELEC.CONN.Size",{"$nulls":3},"1/2\"NPT(F)"]
[25,{"$nulls":3},"单位 Unit",null,null,"m3/h",null,null,"保位阀 Locked Valve"]
[26,null,null,"管道规格 Specification",{"$nulls":3},"DN100",null,null,"备用钢瓶 Spare Cylinder"]
[27,null,null,"管道材料 Material",{"$nulls":3},"S30408",null,null,"制造厂 Manufacturer"]
[28,null,null,"动力粘度 Viscosity  (CP)",{"$nulls":3},1.53]
[29,null,null,"压缩系数 Compress Factor",{"$nulls":6},"备注 Remarks"]
[30,null,null,"气化压力 Vapor Pressure Mpa",{"$nulls":6},"阀门口径、内件、气源接口尺寸等的选择以最终确定的供货商设计计算选型为准。"]
[31,null,null,"临界压力 Critical Press Mpa"]
[32,null,null,"噪音 Noise Level",{"$nulls":6},"带符合工艺及仪表要求的配对法兰，垫片(RPTFE)、紧固件及其它阀内安装附件。"]
[33,null,null,"气源故障阀开/关/保持FC/FO/FL",{"$nulls":3},"FL"]
[34,"阀体/阀芯规格 ",null,"型号 Model"]
[35,"Body/Plug ",null,"阀形式 Valve Style",{"$nulls":3},"球阀"]
[36,"Specification",null,"流开/流关 Flow Open/Close"]
[37,null,null,"阀座数量 Seat NO."]
[38,null,null,"阀芯形式 Plug Type",{"$nulls":3},"浮动O型球"]
[39,null,null,"阀口径 Port size",{"$nulls":3},{"$f":"H580","v":"DN100"}]
[40,null,null,"流量特性 Flow Characteristic",{"$nulls":3},"ON-OFF"]
[41,null,null,"阀体材质 Body Material",{"$nulls":3},"CF8"]
[42,null,null,"阀芯材质 Plug Material",{"$nulls":3},304]
[43,null,null,"阀座材质 Seat Material",{"$nulls":3},304]
[44,null,null,"阀杆材质 Stem Material",{"$nulls":3},630]
[45,null,null,"连接尺寸","尺寸  Size",null,null,{"$f":"H593","v":"DN100"}]
[46,null,null,"Process","标准 Rating",null,null,"HG20592-2009(B) PN16 SO-RF"]
[47,null,null,"connection"]
[48,null,null,"法兰材质 Flange Material",{"$nulls":3},"同阀体"]
[49,null,null,"填料 Packing",{"$nulls":3},"PTFE"]
[50,null,null,"泄漏等级 Leakage Class",{"$nulls":3},"ANSI V"]
[1,"位号 TAG NO.",{"$nulls":5},"1KV-2（205-405）",null,null,"阀盖形式 Bonnet Type",{"$nulls":3},"供应商填写"]
[2,{"$nulls":9},"允许最大压差 Allow △P Mpa(G)",{"$nulls":3},"供应商填写"]
[3,"数量 Q'ty",{"$nulls":5},3,null,null,"最大开度 Open %AT MAX.Flow",{"$nulls":3},"供应商填写"]
[4,"用途   Service",{"$nulls":5},"1P2（201-401）料浆泵出口至1V3202半成品高位槽进料开关阀",null,null,"计算CV  CALC.Cv",{"$nulls":3},"供应商填写"]
[5,{"$nulls":9},"选择CV Selected Cv",{"$nulls":3},"供应商填写"]
[6,"P&ID号 P&ID NO",{"$nulls":5},"20241215-02-GY-03- 02B",null,null,"连接形式 Connection Type",{"$nulls":3},"法兰式"]
[7]
[8,"管道或设备号 LINE ＆ EQUIP.NO.",{"$nulls":5},"1PLS-2203-100-C2S-N",null,null,"执行机构 Actuator"]
[9,{"$nulls":9},"型号 Model"]
[10,"流体参数",null,"介质 ",{"$nulls":3},"工艺固液混合物(PPS+水 )",null,null,"型式 Type",{"$nulls":3},"单作用活塞式"]
[11,"Fluid data",null,"Fluid",{"$nulls":6},"作用形式 Action Style",{"$nulls":3},"气开"]
[12,null,null,"压力","阀前压力",null,null,0.4,null,null,"弹簧范围 Spring Range"]
[13,null,null,"Press","Upstream Pressure",{"$nulls":5},"行程 Travel"]
[14,{"$nulls":3},"阀后压力",null,null,0.36,null,null,"手轮 Hand Wheel",{"$nulls":3},"YES"]
[15,{"$nulls":3},"Downstream Pressure",{"$nulls":5},"供气压力 Air Supply Press",{"$nulls":3},"400~700kpa"]
[16,{"$nulls":3},"阀关闭压差",null,null,0.4,null,null,"气信号接口尺寸 PNEU.CONN.Size",{"$nulls":3},"1/4\"NPT"]
[17,{"$nulls":3},"Shut-off Diff Pressure"]
[18,{"$nulls":3},"单位 Unit",null,null,"Mpa(G)",null,null,"附件 Accessories"]
[19,null,null,"温度 Temp.","操作Oper.",null,null,30,null,null,"过滤减压阀 Regulator ",{"$nulls":3},"YES"]
[20,null,null,"  (Deg. C)","设计Des.",{"$nulls":5},"限位开关 Limited Switch ",{"$nulls":3},"YES"]
[21,null,null,"密度 Density","操作Oper.",null,null,"1040kg/m3",null,null,"电磁阀 Solenoid valve",{"$nulls":3},"二位三通，低功耗"]
[22,null,null,"流量","最小 Min.",{"$nulls":5},"电源 Power Supply",{"$nulls":3},"24VDC"]
[23,null,null,"Flow rate","正常 Nor.",null,null,60,null,null,"防爆等级 Ex.Certification",{"$nulls":3},"ExdIIBT4"]
[24,{"$nulls":3},"最大 Max.",{"$nulls":5},"电气接口尺寸 ELEC.CONN.Size",{"$nulls":3},"1/2\"NPT(F)"]
[25,{"$nulls":3},"单位 Unit",null,null,"m3/h",null,null,"保位阀 Locked Valve"]
[26,null,null,"管道规格 Specification",{"$nulls":3},"DN100",null,null,"备用钢瓶 Spare Cylinder"]
[27,null,null,"管道材料 Material",{"$nulls":3},"S30408",null,null,"制造厂 Manufacturer"]
[28,null,null,"动力粘度 Viscosity  (CP)",{"$nulls":3},1.53]
[29,null,null,"压缩系数 Compress Factor",{"$nulls":6},"备注 Remarks"]
[30,null,null,"气化压力 Vapor Pressure Mpa",{"$nulls":6},"阀门口径、内件、气源接口尺寸等的选择以最终确定的供货商设计计算选型为准。"]
[31,null,null,"临界压力 Critical Press Mpa"]
[32,null,null,"噪音 Noise Level",{"$nulls":6},"带符合工艺及仪表要求的配对法兰，垫片(RPTFE)、紧固件及其它阀内安装附件。"]
[33,null,null,"气源故障阀开/关/保持FC/FO/FL",{"$nulls":3},"FL"]
[34,"阀体/阀芯规格 ",null,"型号 Model"]
[35,"Body/Plug ",null,"阀形式 Valve Style",{"$nulls":3},"球阀"]
[36,"Specification",null,"流开/流关 Flow Open/Close"]
[37,null,null,"阀座数量 Seat NO."]
[38,null,null,"阀芯形式 Plug Type",{"$nulls":3},"浮动O型球"]
[39,null,null,"阀口径 Port size",{"$nulls":3},{"$f":"H630","v":"DN100"}]
[40,null,null,"流量特性 Flow Characteristic",{"$nulls":3},"ON-OFF"]
[41,null,null,"阀体材质 Body Material",{"$nulls":3},"CF8"]
[42,null,null,"阀芯材质 Plug Material",{"$nulls":3},304]
[43,null,null,"阀座材质 Seat Material",{"$nulls":3},304]
[44,null,null,"阀杆材质 Stem Material",{"$nulls":3},630]
[45,null,null,"连接尺寸","尺寸  Size",null,null,{"$f":"H643","v":"DN100"}]
[46,null,null,"Process","标准 Rating",null,null,"HG20592-2009(B) PN16 SO-RF"]
[47,null,null,"connection"]
[48,null,null,"法兰材质 Flange Material",{"$nulls":3},"同阀体"]
[49,null,null,"填料 Packing",{"$nulls":3},"PTFE"]
[50,null,null,"泄漏等级 Leakage Class",{"$nulls":3},"ANSI V"]
[1,"位号 TAG NO.",{"$nulls":5},"1KV-3001",null,null,"阀盖形式 Bonnet Type",{"$nulls":3},"供应商填写"]
[2,{"$nulls":9},"允许最大压差 Allow △P Mpa(G)",{"$nulls":3},"供应商填写"]
[3,"数量 Q'ty",{"$nulls":5},1,null,null,"最大开度 Open %AT MAX.Flow",{"$nulls":3},"供应商填写"]
[4,"用途   Service",{"$nulls":5},"1V3001A混料罐出料开关阀",null,null,"计算CV  CALC.Cv",{"$nulls":3},"供应商填写"]
[5,{"$nulls":9},"选择CV Selected Cv",{"$nulls":3},"供应商填写"]
[6,"P&ID号 P&ID NO",{"$nulls":5},"20241215-03-GY-03- 01",null,null,"连接形式 Connection Type",{"$nulls":3},"法兰式"]
[7]
[8,"管道或设备号 LINE ＆ EQUIP.NO.",{"$nulls":5},"1PLS-3103-100-C2S-N",null,null,"执行机构 Actuator"]
[9,{"$nulls":9},"型号 Model"]
[10,"流体参数",null,"介质 ",{"$nulls":3},"工艺固液混合物(PPS+水 )",null,null,"型式 Type",{"$nulls":3},"单作用活塞式"]
[11,"Fluid data",null,"Fluid",{"$nulls":6},"作用形式 Action Style",{"$nulls":3},"气开"]
[12,null,null,"压力","阀前压力",null,null,0.04,null,null,"弹簧范围 Spring Range"]
[13,null,null,"Press","Upstream Pressure",{"$nulls":5},"行程 Travel"]
[14,{"$nulls":3},"阀后压力",null,null,0.02,null,null,"手轮 Hand Wheel",{"$nulls":3},"YES"]
[15,{"$nulls":3},"Downstream Pressure",{"$nulls":5},"供气压力 Air Supply Press",{"$nulls":3},"400~700kpa"]
[16,{"$nulls":3},"阀关闭压差",null,null,0.04,null,null,"气信号接口尺寸 PNEU.CONN.Size",{"$nulls":3},"1/4\"NPT"]
[17,{"$nulls":3},"Shut-off Diff Pressure"]
[18,{"$nulls":3},"单位 Unit",null,null,"Mpa(G)",null,null,"附件 Accessories"]
[19,null,null,"温度 Temp.","操作Oper.",null,null,30,null,null,"过滤减压阀 Regulator ",{"$nulls":3},"YES"]
[20,null,null,"  (Deg. C)","设计Des.",{"$nulls":5},"限位开关 Limited Switch ",{"$nulls":3},"YES"]
[21,null,null,"密度 Density","操作Oper.",null,null,"1040kg/m3",null,null,"电磁阀 Solenoid valve",{"$nulls":3},"二位三通，低功耗"]
[22,null,null,"流量","最小 Min.",{"$nulls":5},"电源 Power Supply",{"$nulls":3},"24VDC"]
[23,null,null,"Flow rate","正常 Nor.",null,null,30,null,null,"防爆等级 Ex.Certification",{"$nulls":3},"ExdIIBT4"]
[24,{"$nulls":3},"最大 Max.",{"$nulls":5},"电气接口尺寸 ELEC.CONN.Size",{"$nulls":3},"1/2\"NPT(F)"]
[25,{"$nulls":3},"单位 Unit",null,null,"m3/h",null,null,"保位阀 Locked Valve"]
[26,null,null,"管道规格 Specification",{"$nulls":3},"DN100",null,null,"备用钢瓶 Spare Cylinder"]
[27,null,null,"管道材料 Material",{"$nulls":3},"S30408",null,null,"制造厂 Manufacturer"]
[28,null,null,"动力粘度 Viscosity  (CP)",{"$nulls":3},1.53]
[29,null,null,"压缩系数 Compress Factor",{"$nulls":6},"备注 Remarks"]
[30,null,null,"气化压力 Vapor Pressure Mpa",{"$nulls":6},"阀门口径、内件、气源接口尺寸等的选择以最终确定的供货商设计计算选型为准。"]
[31,null,null,"临界压力 Critical Press Mpa"]
[32,null,null,"噪音 Noise Level",{"$nulls":6},"带符合工艺及仪表要求的配对法兰，垫片(RPTFE)、紧固件及其它阀内安装附件。"]
[33,null,null,"气源故障阀开/关/保持FC/FO/FL",{"$nulls":3},"FC"]
[34,"阀体/阀芯规格 ",null,"型号 Model"]
[35,"Body/Plug ",null,"阀形式 Valve Style",{"$nulls":3},"球阀"]
[36,"Specification",null,"流开/流关 Flow Open/Close"]
[37,null,null,"阀座数量 Seat NO."]
[38,null,null,"阀芯形式 Plug Type",{"$nulls":3},"浮动O型球"]
[39,null,null,"阀口径 Port size",{"$nulls":3},{"$f":"H680","v":"DN100"}]
[40,null,null,"流量特性 Flow Characteristic",{"$nulls":3},"ON-OFF"]
[41,null,null,"阀体材质 Body Material",{"$nulls":3},"CF8"]
[42,null,null,"阀芯材质 Plug Material",{"$nulls":3},304]
[43,null,null,"阀座材质 Seat Material",{"$nulls":3},304]
[44,null,null,"阀杆材质 Stem Material",{"$nulls":3},630]
[45,null,null,"连接尺寸","尺寸  Size",null,null,{"$f":"H693","v":"DN100"}]
[46,null,null,"Process","标准 Rating",null,null,"HG20592-2009(B) PN16 SO-RF"]
[47,null,null,"connection"]
[48,null,null,"法兰材质 Flange Material",{"$nulls":3},"同阀体"]
[49,null,null,"填料 Packing",{"$nulls":3},"PTFE"]
[50,null,null,"泄漏等级 Leakage Class",{"$nulls":3},"ANSI V"]
[1,"位号 TAG NO.",{"$nulls":5},"1KV-3002",null,null,"阀盖形式 Bonnet Type",{"$nulls":3},"供应商填写"]
[2,{"$nulls":9},"允许最大压差 Allow △P Mpa(G)",{"$nulls":3},"供应商填写"]
[3,"数量 Q'ty",{"$nulls":5},1,null,null,"最大开度 Open %AT MAX.Flow",{"$nulls":3},"供应商填写"]
[4,"用途   Service",{"$nulls":5},"1V3102半成品高位槽进料开关阀",null,null,"计算CV  CALC.Cv",{"$nulls":3},"供应商填写"]
[5,{"$nulls":9},"选择CV Selected Cv",{"$nulls":3},"供应商填写"]
[6,"P&ID号 P&ID NO",{"$nulls":5},"20241215-03-GY-03- 01",null,null,"连接形式 Connection Type",{"$nulls":3},"法兰式"]
[7]
[8,"管道或设备号 LINE ＆ EQUIP.NO.",{"$nulls":5},"1PLS-3103-100-C2S-N",null,null,"执行机构 Actuator"]
[9,{"$nulls":9},"型号 Model"]
[10,"流体参数",null,"介质 ",{"$nulls":3},"工艺固液混合物(PPS+水 )",null,null,"型式 Type",{"$nulls":3},"单作用活塞式"]
[11,"Fluid data",null,"Fluid",{"$nulls":6},"作用形式 Action Style",{"$nulls":3},"气开"]
[12,null,null,"压力","阀前压力",null,null,0.04,null,null,"弹簧范围 Spring Range"]
[13,null,null,"Press","Upstream Pressure",{"$nulls":5},"行程 Travel"]
[14,{"$nulls":3},"阀后压力",null,null,0.02,null,null,"手轮 Hand Wheel",{"$nulls":3},"YES"]
[15,{"$nulls":3},"Downstream Pressure",{"$nulls":5},"供气压力 Air Supply Press",{"$nulls":3},"400~700kpa"]
[16,{"$nulls":3},"阀关闭压差",null,null,0.04,null,null,"气信号接口尺寸 PNEU.CONN.Size",{"$nulls":3},"1/4\"NPT"]
[17,{"$nulls":3},"Shut-off Diff Pressure"]
[18,{"$nulls":3},"单位 Unit",null,null,"Mpa(G)",null,null,"附件 Accessories"]
[19,null,null,"温度 Temp.","操作Oper.",null,null,30,null,null,"过滤减压阀 Regulator ",{"$nulls":3},"YES"]
[20,null,null,"  (Deg. C)","设计Des.",{"$nulls":5},"限位开关 Limited Switch ",{"$nulls":3},"YES"]
[21,null,null,"密度 Density","操作Oper.",null,null,"1040kg/m3",null,null,"电磁阀 Solenoid valve",{"$nulls":3},"二位三通，低功耗"]
[22,null,null,"流量","最小 Min.",{"$nulls":5},"电源 Power Supply",{"$nulls":3},"24VDC"]
[23,null,null,"Flow rate","正常 Nor.",null,null,30,null,null,"防爆等级 Ex.Certification",{"$nulls":3},"ExdIIBT4"]
[24,{"$nulls":3},"最大 Max.",{"$nulls":5},"电气接口尺寸 ELEC.CONN.Size",{"$nulls":3},"1/2\"NPT(F)"]
[25,{"$nulls":3},"单位 Unit",null,null,"m3/h",null,null,"保位阀 Locked Valve"]
[26,null,null,"管道规格 Specification",{"$nulls":3},"DN100",null,null,"备用钢瓶 Spare Cylinder"]
[27,null,null,"管道材料 Material",{"$nulls":3},"S30408",null,null,"制造厂 Manufacturer"]
[28,null,null,"动力粘度 Viscosity  (CP)",{"$nulls":3},1.53]
[29,null,null,"压缩系数 Compress Factor",{"$nulls":6},"备注 Remarks"]
[30,null,null,"气化压力 Vapor Pressure Mpa",{"$nulls":6},"阀门口径、内件、气源接口尺寸等的选择以最终确定的供货商设计计算选型为准。"]
[31,null,null,"临界压力 Critical Press Mpa"]
[32,null,null,"噪音 Noise Level",{"$nulls":6},"带符合工艺及仪表要求的配对法兰，垫片(RPTFE)、紧固件及其它阀内安装附件。"]
[33,null,null,"气源故障阀开/关/保持FC/FO/FL",{"$nulls":3},"FC"]
[34,"阀体/阀芯规格 ",null,"型号 Model"]
[35,"Body/Plug ",null,"阀形式 Valve Style",{"$nulls":3},"球阀"]
[36,"Specification",null,"流开/流关 Flow Open/Close"]
[37,null,null,"阀座数量 Seat NO."]
[38,null,null,"阀芯形式 Plug Type",{"$nulls":3},"浮动O型球"]
[39,null,null,"阀口径 Port size",{"$nulls":3},{"$f":"H730","v":"DN100"}]
[40,null,null,"流量特性 Flow Characteristic",{"$nulls":3},"ON-OFF"]
[41,null,null,"阀体材质 Body Material",{"$nulls":3},"CF8"]
[42,null,null,"阀芯材质 Plug Material",{"$nulls":3},304]
[43,null,null,"阀座材质 Seat Material",{"$nulls":3},304]
[44,null,null,"阀杆材质 Stem Material",{"$nulls":3},630]
[45,null,null,"连接尺寸","尺寸  Size",null,null,{"$f":"H743","v":"DN100"}]
[46,null,null,"Process","标准 Rating",null,null,"HG20592-2009(B) PN16 SO-RF"]
[47,null,null,"connection"]
[48,null,null,"法兰材质 Flange Material",{"$nulls":3},"同阀体"]
[49,null,null,"填料 Packing",{"$nulls":3},"PTFE"]
[50,null,null,"泄漏等级 Leakage Class",{"$nulls":3},"ANSI V"]
[1,"位号 TAG NO.",{"$nulls":5},"1KV-3003",null,null,"阀盖形式 Bonnet Type",{"$nulls":3},"供应商填写"]
[2,{"$nulls":9},"允许最大压差 Allow △P Mpa(G)",{"$nulls":3},"供应商填写"]
[3,"数量 Q'ty",{"$nulls":5},1,null,null,"最大开度 Open %AT MAX.Flow",{"$nulls":3},"供应商填写"]
[4,"用途   Service",{"$nulls":5},"1V3202半成品高位槽进料开关阀",null,null,"计算CV  CALC.Cv",{"$nulls":3},"供应商填写"]
[5,{"$nulls":9},"选择CV Selected Cv",{"$nulls":3},"供应商填写"]
[6,"P&ID号 P&ID NO",{"$nulls":5},"20241215-03-GY-03- 01",null,null,"连接形式 Connection Type",{"$nulls":3},"法兰式"]
[7]
[8,"管道或设备号 LINE ＆ EQUIP.NO.",{"$nulls":5},"1PLS-3203-100-C2S-N",null,null,"执行机构 Actuator"]
[9,{"$nulls":9},"型号 Model"]
[10,"流体参数",null,"介质 ",{"$nulls":3},"工艺固液混合物(PPS+水 )",null,null,"型式 Type",{"$nulls":3},"单作用活塞式"]
[11,"Fluid data",null,"Fluid",{"$nulls":6},"作用形式 Action Style",{"$nulls":3},"气开"]
[12,null,null,"压力","阀前压力",null,null,0.04,null,null,"弹簧范围 Spring Range"]
[13,null,null,"Press","Upstream Pressure",{"$nulls":5},"行程 Travel"]
[14,{"$nulls":3},"阀后压力",null,null,0.02,null,null,"手轮 Hand Wheel",{"$nulls":3},"YES"]
[15,{"$nulls":3},"Downstream Pressure",{"$nulls":5},"供气压力 Air Supply Press",{"$nulls":3},"400~700kpa"]
[16,{"$nulls":3},"阀关闭压差",null,null,0.04,null,null,"气信号接口尺寸 PNEU.CONN.Size",{"$nulls":3},"1/4\"NPT"]
[17,{"$nulls":3},"Shut-off Diff Pressure"]
[18,{"$nulls":3},"单位 Unit",null,null,"Mpa(G)",null,null,"附件 Accessories"]
[19,null,null,"温度 Temp.","操作Oper.",null,null,30,null,null,"过滤减压阀 Regulator ",{"$nulls":3},"YES"]
[20,null,null,"  (Deg. C)","设计Des.",{"$nulls":5},"限位开关 Limited Switch ",{"$nulls":3},"YES"]
[21,null,null,"密度 Density","操作Oper.",null,null,"1040kg/m3",null,null,"电磁阀 Solenoid valve",{"$nulls":3},"二位三通，低功耗"]
[22,null,null,"流量","最小 Min.",{"$nulls":5},"电源 Power Supply",{"$nulls":3},"24VDC"]
[23,null,null,"Flow rate","正常 Nor.",null,null,30,null,null,"防爆等级 Ex.Certification",{"$nulls":3},"ExdIIBT4"]
[24,{"$nulls":3},"最大 Max.",{"$nulls":5},"电气接口尺寸 ELEC.CONN.Size",{"$nulls":3},"1/2\"NPT(F)"]
[25,{"$nulls":3},"单位 Unit",null,null,"m3/h",null,null,"保位阀 Locked Valve"]
[26,null,null,"管道规格 Specification",{"$nulls":3},"DN100",null,null,"备用钢瓶 Spare Cylinder"]
[27,null,null,"管道材料 Material",{"$nulls":3},"S30408",null,null,"制造厂 Manufacturer"]
[28,null,null,"动力粘度 Viscosity  (CP)",{"$nulls":3},1.53]
[29,null,null,"压缩系数 Compress Factor",{"$nulls":6},"备注 Remarks"]
[30,null,null,"气化压力 Vapor Pressure Mpa",{"$nulls":6},"阀门口径、内件、气源接口尺寸等的选择以最终确定的供货商设计计算选型为准。"]
[31,null,null,"临界压力 Critical Press Mpa"]
[32,null,null,"噪音 Noise Level",{"$nulls":6},"带符合工艺及仪表要求的配对法兰，垫片(RPTFE)、紧固件及其它阀内安装附件。"]
[33,null,null,"气源故障阀开/关/保持FC/FO/FL",{"$nulls":3},"FC"]
[34,"阀体/阀芯规格 ",null,"型号 Model"]
[35,"Body/Plug ",null,"阀形式 Valve Style",{"$nulls":3},"球阀"]
[36,"Specification",null,"流开/流关 Flow Open/Close"]
[37,null,null,"阀座数量 Seat NO."]
[38,null,null,"阀芯形式 Plug Type",{"$nulls":3},"浮动O型球"]
[39,null,null,"阀口径 Port size",{"$nulls":3},{"$f":"H780","v":"DN100"}]
[40,null,null,"流量特性 Flow Characteristic",{"$nulls":3},"ON-OFF"]
[41,null,null,"阀体材质 Body Material",{"$nulls":3},"CF8"]
[42,null,null,"阀芯材质 Plug Material",{"$nulls":3},"304+ST"]
[43,null,null,"阀座材质 Seat Material",{"$nulls":3},304]
[44,null,null,"阀杆材质 Stem Material",{"$nulls":3},630]
[45,null,null,"连接尺寸","尺寸  Size",null,null,{"$f":"H793","v":"DN100"}]
[46,null,null,"Process","标准 Rating",null,null,"HG20592-2009(B) PN16 SO-RF"]
[47,null,null,"connection"]
[48,null,null,"法兰材质 Flange Material",{"$nulls":3},"同阀体"]
[49,null,null,"填料 Packing",{"$nulls":3},"PTFE"]
[50,null,null,"泄漏等级 Leakage Class",{"$nulls":3},"ANSI V"]
[1,"位号 TAG NO.",{"$nulls":5},"1KV-3004",null,null,"阀盖形式 Bonnet Type",{"$nulls":3},"供应商填写"]
[2,{"$nulls":9},"允许最大压差 Allow △P Mpa(G)",{"$nulls":3},"供应商填写"]
[3,"数量 Q'ty",{"$nulls":5},1,null,null,"最大开度 Open %AT MAX.Flow",{"$nulls":3},"供应商填写"]
[4,"用途   Service",{"$nulls":5},"1V3302半成品高位槽进料开关阀",null,null,"计算CV  CALC.Cv",{"$nulls":3},"供应商填写"]
[5,{"$nulls":9},"选择CV Selected Cv",{"$nulls":3},"供应商填写"]
[6,"P&ID号 P&ID NO",{"$nulls":5},"20241215-03-GY-03- 01",null,null,"连接形式 Connection Type",{"$nulls":3},"法兰式"]
[7]
[8,"管道或设备号 LINE ＆ EQUIP.NO.",{"$nulls":5},"1PLS-3303-100-C2S-N",null,null,"执行机构 Actuator"]
[9,{"$nulls":9},"型号 Model"]
[10,"流体参数",null,"介质 ",{"$nulls":3},"工艺固液混合物(PPS+水 )",null,null,"型式 Type",{"$nulls":3},"单作用活塞式"]
[11,"Fluid data",null,"Fluid",{"$nulls":6},"作用形式 Action Style",{"$nulls":3},"气开"]
[12,null,null,"压力","阀前压力",null,null,0.04,null,null,"弹簧范围 Spring Range"]
[13,null,null,"Press","Upstream Pressure",{"$nulls":5},"行程 Travel"]
[14,{"$nulls":3},"阀后压力",null,null,0.02,null,null,"手轮 Hand Wheel",{"$nulls":3},"YES"]
[15,{"$nulls":3},"Downstream Pressure",{"$nulls":5},"供气压力 Air Supply Press",{"$nulls":3},"400~700kpa"]
[16,{"$nulls":3},"阀关闭压差",null,null,0.04,null,null,"气信号接口尺寸 PNEU.CONN.Size",{"$nulls":3},"1/4\"NPT"]
[17,{"$nulls":3},"Shut-off Diff Pressure"]
[18,{"$nulls":3},"单位 Unit",null,null,"Mpa(G)",null,null,"附件 Accessories"]
[19,null,null,"温度 Temp.","操作Oper.",null,null,30,null,null,"过滤减压阀 Regulator ",{"$nulls":3},"YES"]
[20,null,null,"  (Deg. C)","设计Des.",{"$nulls":5},"限位开关 Limited Switch ",{"$nulls":3},"YES"]
[21,null,null,"密度 Density","操作Oper.",null,null,"1040kg/m3",null,null,"电磁阀 Solenoid valve",{"$nulls":3},"二位三通，低功耗"]
[22,null,null,"流量","最小 Min.",{"$nulls":5},"电源 Power Supply",{"$nulls":3},"24VDC"]
[23,null,null,"Flow rate","正常 Nor.",null,null,30,null,null,"防爆等级 Ex.Certification",{"$nulls":3},"ExdIIBT4"]
[24,{"$nulls":3},"最大 Max.",{"$nulls":5},"电气接口尺寸 ELEC.CONN.Size",{"$nulls":3},"1/2\"NPT(F)"]
[25,{"$nulls":3},"单位 Unit",null,null,"m3/h",null,null,"保位阀 Locked Valve"]
[26,null,null,"管道规格 Specification",{"$nulls":3},"DN100",null,null,"备用钢瓶 Spare Cylinder"]
[27,null,null,"管道材料 Material",{"$nulls":3},"S30408",null,null,"制造厂 Manufacturer"]
[28,null,null,"动力粘度 Viscosity  (CP)",{"$nulls":3},1.53]
[29,null,null,"压缩系数 Compress Factor",{"$nulls":6},"备注 Remarks"]
[30,null,null,"气化压力 Vapor Pressure Mpa",{"$nulls":6},"阀门口径、内件、气源接口尺寸等的选择以最终确定的供货商设计计算选型为准。"]
[31,null,null,"临界压力 Critical Press Mpa"]
[32,null,null,"噪音 Noise Level",{"$nulls":6},"带符合工艺及仪表要求的配对法兰，垫片(RPTFE)、紧固件及其它阀内安装附件。"]
[33,null,null,"气源故障阀开/关/保持FC/FO/FL",{"$nulls":3},"FC"]
[34,"阀体/阀芯规格 ",null,"型号 Model"]
[35,"Body/Plug ",null,"阀形式 Valve Style",{"$nulls":3},"球阀"]
[36,"Specification",null,"流开/流关 Flow Open/Close"]
[37,null,null,"阀座数量 Seat NO."]
[38,null,null,"阀芯形式 Plug Type",{"$nulls":3},"浮动O型球"]
[39,null,null,"阀口径 Port size",{"$nulls":3},{"$f":"H830","v":"DN100"}]
[40,null,null,"流量特性 Flow Characteristic",{"$nulls":3},"ON-OFF"]
[41,null,null,"阀体材质 Body Material",{"$nulls":3},"CF8"]
[42,null,null,"阀芯材质 Plug Material",{"$nulls":3},304]
[43,null,null,"阀座材质 Seat Material",{"$nulls":3},304]
[44,null,null,"阀杆材质 Stem Material",{"$nulls":3},630]
[45,null,null,"连接尺寸","尺寸  Size",null,null,{"$f":"H843","v":"DN100"}]
[46,null,null,"Process","标准 Rating",null,null,"HG20592-2009(B) PN16 SO-RF"]
[47,null,null,"connection"]
[48,null,null,"法兰材质 Flange Material",{"$nulls":3},"同阀体"]
[49,null,null,"填料 Packing",{"$nulls":3},"PTFE"]
[50,null,null,"泄漏等级 Leakage Class",{"$nulls":3},"ANSI V"]
[1,"位号 TAG NO.",{"$nulls":5},"1KV-3005",null,null,"阀盖形式 Bonnet Type",{"$nulls":3},"供应商填写"]
[2,{"$nulls":9},"允许最大压差 Allow △P Mpa(G)",{"$nulls":3},"供应商填写"]
[3,"数量 Q'ty",{"$nulls":5},1,null,null,"最大开度 Open %AT MAX.Flow",{"$nulls":3},"供应商填写"]
[4,"用途   Service",{"$nulls":5},"1V3001A混料罐氮气反吹开关阀",null,null,"计算CV  CALC.Cv",{"$nulls":3},"供应商填写"]
[5,{"$nulls":9},"选择CV Selected Cv",{"$nulls":3},"供应商填写"]
[6,"P&ID号 P&ID NO",{"$nulls":5},"20241215-03-GY-03- 01",null,null,"连接形式 Connection Type",{"$nulls":3},"法兰式"]
[7]
[8,"管道或设备号 LINE ＆ EQUIP.NO.",{"$nulls":5},"1N1-3001-25-C2S-N",null,null,"执行机构 Actuator"]
[9,{"$nulls":9},"型号 Model"]
[10,"流体参数",null,"介质 ",{"$nulls":3},"氮气",null,null,"型式 Type",{"$nulls":3},"单作用活塞式"]
[11,"Fluid data",null,"Fluid",{"$nulls":6},"作用形式 Action Style",{"$nulls":3},"气开"]
[12,null,null,"压力","阀前压力",null,null,0.4,null,null,"弹簧范围 Spring Range"]
[13,null,null,"Press","Upstream Pressure",{"$nulls":5},"行程 Travel"]
[14,{"$nulls":3},"阀后压力",null,null,0.36,null,null,"手轮 Hand Wheel",{"$nulls":3},"YES"]
[15,{"$nulls":3},"Downstream Pressure",{"$nulls":5},"供气压力 Air Supply Press",{"$nulls":3},"400~700kpa"]
[16,{"$nulls":3},"阀关闭压差",null,null,0.4,null,null,"气信号接口尺寸 PNEU.CONN.Size",{"$nulls":3},"1/4\"NPT"]
[17,{"$nulls":3},"Shut-off Diff Pressure"]
[18,{"$nulls":3},"单位 Unit",null,null,"Mpa(G)",null,null,"附件 Accessories"]
[19,null,null,"温度 Temp.","操作Oper.",null,null,"常温",null,null,"过滤减压阀 Regulator ",{"$nulls":3},"YES"]
[20,null,null,"  (Deg. C)","设计Des.",{"$nulls":5},"限位开关 Limited Switch ",{"$nulls":3},"YES"]
[21,null,null,"密度 Density","操作Oper.",null,null,"1.24kg/m3（标）",null,null,"电磁阀 Solenoid valve",{"$nulls":3},"二位三通，低功耗"]
[22,null,null,"流量","最小 Min.",{"$nulls":5},"电源 Power Supply",{"$nulls":3},"24VDC"]
[23,null,null,"Flow rate","正常 Nor.",null,null,15,null,null,"防爆等级 Ex.Certification",{"$nulls":3},"ExdIIBT4"]
[24,{"$nulls":3},"最大 Max.",{"$nulls":5},"电气接口尺寸 ELEC.CONN.Size",{"$nulls":3},"1/2\"NPT(F)"]
[25,{"$nulls":3},"单位 Unit",null,null,"m3/h",null,null,"保位阀 Locked Valve"]
[26,null,null,"管道规格 Specification",{"$nulls":3},"DN25",null,null,"备用钢瓶 Spare Cylinder"]
[27,null,null,"管道材料 Material",{"$nulls":3},"S30408",null,null,"制造厂 Manufacturer"]
[28,null,null,"动力粘度 Viscosity  (CP)"]
[29,null,null,"压缩系数 Compress Factor",{"$nulls":6},"备注 Remarks"]
[30,null,null,"气化压力 Vapor Pressure Mpa",{"$nulls":6},"阀门口径、内件、气源接口尺寸等的选择以最终确定的供货商设计计算选型为准。"]
[31,null,null,"临界压力 Critical Press Mpa"]
[32,null,null,"噪音 Noise Level",{"$nulls":6},"带符合工艺及仪表要求的配对法兰，垫片(RPTFE)、紧固件及其它阀内安装附件。"]
[33,null,null,"气源故障阀开/关/保持FC/FO/FL",{"$nulls":3},"FC"]
[34,"阀体/阀芯规格 ",null,"型号 Model"]
[35,"Body/Plug ",null,"阀形式 Valve Style",{"$nulls":3},"球阀"]
[36,"Specification",null,"流开/流关 Flow Open/Close"]
[37,null,null,"阀座数量 Seat NO."]
[38,null,null,"阀芯形式 Plug Type",{"$nulls":3},"浮动O型球"]
[39,null,null,"阀口径 Port size",{"$nulls":3},{"$f":"H880","v":"DN25"}]
[40,null,null,"流量特性 Flow Characteristic",{"$nulls":3},"ON-OFF"]
[41,null,null,"阀体材质 Body Material",{"$nulls":3},"CF8"]
[42,null,null,"阀芯材质 Plug Material",{"$nulls":3},304]
[43,null,null,"阀座材质 Seat Material",{"$nulls":3},304]
[44,null,null,"阀杆材质 Stem Material",{"$nulls":3},630]
[45,null,null,"连接尺寸","尺寸  Size",null,null,{"$f":"H893","v":"DN25"}]
[46,null,null,"Process","标准 Rating",null,null,"HG20592-2009(B) PN16 SO-RF"]
[47,null,null,"connection"]
[48,null,null,"法兰材质 Flange Material",{"$nulls":3},"同阀体"]
[49,null,null,"填料 Packing",{"$nulls":3},"PTFE"]
[50,null,null,"泄漏等级 Leakage Class",{"$nulls":3},"ANSI V"]
[1,"位号 TAG NO.",{"$nulls":5},"1KV-3006",null,null,"阀盖形式 Bonnet Type",{"$nulls":3},"供应商填写"]
[2,{"$nulls":9},"允许最大压差 Allow △P Mpa(G)",{"$nulls":3},"供应商填写"]
[3,"数量 Q'ty",{"$nulls":5},1,null,null,"最大开度 Open %AT MAX.Flow",{"$nulls":3},"供应商填写"]
[4,"用途   Service",{"$nulls":5},"1V3001B混料罐出料开关阀",null,null,"计算CV  CALC.Cv",{"$nulls":3},"供应商填写"]
[5,{"$nulls":9},"选择CV Selected Cv",{"$nulls":3},"供应商填写"]
[6,"P&ID号 P&ID NO",{"$nulls":5},"20241215-03-GY-03- 01",null,null,"连接形式 Connection Type",{"$nulls":3},"法兰式"]
[7]
[8,"管道或设备号 LINE ＆ EQUIP.NO.",{"$nulls":5},"1PLS-3403-100-C2S-N",null,null,"执行机构 Actuator"]
[9,{"$nulls":9},"型号 Model"]
[10,"流体参数",null,"介质 ",{"$nulls":3},"工艺固液混合物(PPS+水 )",null,null,"型式 Type",{"$nulls":3},"单作用活塞式"]
[11,"Fluid data",null,"Fluid",{"$nulls":6},"作用形式 Action Style",{"$nulls":3},"气开"]
[12,null,null,"压力","阀前压力",null,null,0.04,null,null,"弹簧范围 Spring Range"]
[13,null,null,"Press","Upstream Pressure",{"$nulls":5},"行程 Travel"]
[14,{"$nulls":3},"阀后压力",null,null,0.02,null,null,"手轮 Hand Wheel",{"$nulls":3},"YES"]
[15,{"$nulls":3},"Downstream Pressure",{"$nulls":5},"供气压力 Air Supply Press",{"$nulls":3},"400~700kpa"]
[16,{"$nulls":3},"阀关闭压差",null,null,0.04,null,null,"气信号接口尺寸 PNEU.CONN.Size",{"$nulls":3},"1/4\"NPT"]
[17,{"$nulls":3},"Shut-off Diff Pressure"]
[18,{"$nulls":3},"单位 Unit",null,null,"Mpa(G)",null,null,"附件 Accessories"]
[19,null,null,"温度 Temp.","操作Oper.",null,null,30,null,null,"过滤减压阀 Regulator ",{"$nulls":3},"YES"]
[20,null,null,"  (Deg. C)","设计Des.",{"$nulls":5},"限位开关 Limited Switch ",{"$nulls":3},"YES"]
[21,null,null,"密度 Density","操作Oper.",null,null,"1040kg/m3",null,null,"电磁阀 Solenoid valve",{"$nulls":3},"二位三通，低功耗"]
[22,null,null,"流量","最小 Min.",{"$nulls":5},"电源 Power Supply",{"$nulls":3},"24VDC"]
[23,null,null,"Flow rate","正常 Nor.",null,null,30,null,null,"防爆等级 Ex.Certification",{"$nulls":3},"ExdIIBT4"]
[24,{"$nulls":3},"最大 Max.",{"$nulls":5},"电气接口尺寸 ELEC.CONN.Size",{"$nulls":3},"1/2\"NPT(F)"]
[25,{"$nulls":3},"单位 Unit",null,null,"m3/h",null,null,"保位阀 Locked Valve"]
[26,null,null,"管道规格 Specification",{"$nulls":3},"DN100",null,null,"备用钢瓶 Spare Cylinder"]
[27,null,null,"管道材料 Material",{"$nulls":3},"S30408",null,null,"制造厂 Manufacturer"]
[28,null,null,"动力粘度 Viscosity  (CP)",{"$nulls":3},1.53]
[29,null,null,"压缩系数 Compress Factor",{"$nulls":6},"备注 Remarks"]
[30,null,null,"气化压力 Vapor Pressure Mpa",{"$nulls":6},"阀门口径、内件、气源接口尺寸等的选择以最终确定的供货商设计计算选型为准。"]
[31,null,null,"临界压力 Critical Press Mpa"]
[32,null,null,"噪音 Noise Level",{"$nulls":6},"带符合工艺及仪表要求的配对法兰，垫片(RPTFE)、紧固件及其它阀内安装附件。"]
[33,null,null,"气源故障阀开/关/保持FC/FO/FL",{"$nulls":3},"FC"]
[34,"阀体/阀芯规格 ",null,"型号 Model"]
[35,"Body/Plug ",null,"阀形式 Valve Style",{"$nulls":3},"球阀"]
[36,"Specification",null,"流开/流关 Flow Open/Close"]
[37,null,null,"阀座数量 Seat NO."]
[38,null,null,"阀芯形式 Plug Type",{"$nulls":3},"浮动O型球"]
[39,null,null,"阀口径 Port size",{"$nulls":3},{"$f":"H930","v":"DN100"}]
[40,null,null,"流量特性 Flow Characteristic",{"$nulls":3},"ON-OFF"]
[41,null,null,"阀体材质 Body Material",{"$nulls":3},"CF8"]
[42,null,null,"阀芯材质 Plug Material",{"$nulls":3},304]
[43,null,null,"阀座材质 Seat Material",{"$nulls":3},304]
[44,null,null,"阀杆材质 Stem Material",{"$nulls":3},630]
[45,null,null,"连接尺寸","尺寸  Size",null,null,{"$f":"H943","v":"DN100"}]
[46,null,null,"Process","标准 Rating",null,null,"HG20592-2009(B) PN16 SO-RF"]
[47,null,null,"connection"]
[48,null,null,"法兰材质 Flange Material",{"$nulls":3},"同阀体"]
[49,null,null,"填料 Packing",{"$nulls":3},"PTFE"]
[50,null,null,"泄漏等级 Leakage Class",{"$nulls":3},"ANSI V"]
[1,"位号 TAG NO.",{"$nulls":5},"1KV-3007",null,null,"阀盖形式 Bonnet Type",{"$nulls":3},"供应商填写"]
[2,{"$nulls":9},"允许最大压差 Allow △P Mpa(G)",{"$nulls":3},"供应商填写"]
[3,"数量 Q'ty",{"$nulls":5},1,null,null,"最大开度 Open %AT MAX.Flow",{"$nulls":3},"供应商填写"]
[4,"用途   Service",{"$nulls":5},"1V3402半成品高位槽进料开关阀",null,null,"计算CV  CALC.Cv",{"$nulls":3},"供应商填写"]
[5,{"$nulls":9},"选择CV Selected Cv",{"$nulls":3},"供应商填写"]
[6,"P&ID号 P&ID NO",{"$nulls":5},"20241215-03-GY-03- 01",null,null,"连接形式 Connection Type",{"$nulls":3},"法兰式"]
[7]
[8,"管道或设备号 LINE ＆ EQUIP.NO.",{"$nulls":5},"1PLS-3403-100-C2S-N",null,null,"执行机构 Actuator"]
[9,{"$nulls":9},"型号 Model"]
[10,"流体参数",null,"介质 ",{"$nulls":3},"工艺固液混合物(PPS+水 )",null,null,"型式 Type",{"$nulls":3},"单作用活塞式"]
[11,"Fluid data",null,"Fluid",{"$nulls":6},"作用形式 Action Style",{"$nulls":3},"气开"]
[12,null,null,"压力","阀前压力",null,null,0.04,null,null,"弹簧范围 Spring Range"]
[13,null,null,"Press","Upstream Pressure",{"$nulls":5},"行程 Travel"]
[14,{"$nulls":3},"阀后压力",null,null,0.02,null,null,"手轮 Hand Wheel",{"$nulls":3},"YES"]
[15,{"$nulls":3},"Downstream Pressure",{"$nulls":5},"供气压力 Air Supply Press",{"$nulls":3},"400~700kpa"]
[16,{"$nulls":3},"阀关闭压差",null,null,0.04,null,null,"气信号接口尺寸 PNEU.CONN.Size",{"$nulls":3},"1/4\"NPT"]
[17,{"$nulls":3},"Shut-off Diff Pressure"]
[18,{"$nulls":3},"单位 Unit",null,null,"Mpa(G)",null,null,"附件 Accessories"]
[19,null,null,"温度 Temp.","操作Oper.",null,null,30,null,null,"过滤减压阀 Regulator ",{"$nulls":3},"YES"]
[20,null,null,"  (Deg. C)","设计Des.",{"$nulls":5},"限位开关 Limited Switch ",{"$nulls":3},"YES"]
[21,null,null,"密度 Density","操作Oper.",null,null,"1040kg/m3",null,null,"电磁阀 Solenoid valve",{"$nulls":3},"二位三通，低功耗"]
[22,null,null,"流量","最小 Min.",{"$nulls":5},"电源 Power Supply",{"$nulls":3},"24VDC"]
[23,null,null,"Flow rate","正常 Nor.",null,null,30,null,null,"防爆等级 Ex.Certification",{"$nulls":3},"ExdIIBT4"]
[24,{"$nulls":3},"最大 Max.",{"$nulls":5},"电气接口尺寸 ELEC.CONN.Size",{"$nulls":3},"1/2\"NPT(F)"]
[25,{"$nulls":3},"单位 Unit",null,null,"m3/h",null,null,"保位阀 Locked Valve"]
[26,null,null,"管道规格 Specification",{"$nulls":3},"DN100",null,null,"备用钢瓶 Spare Cylinder"]
[27,null,null,"管道材料 Material",{"$nulls":3},"S30408",null,null,"制造厂 Manufacturer"]
[28,null,null,"动力粘度 Viscosity  (CP)",{"$nulls":3},1.53]
[29,null,null,"压缩系数 Compress Factor",{"$nulls":6},"备注 Remarks"]
[30,null,null,"气化压力 Vapor Pressure Mpa",{"$nulls":6},"阀门口径、内件、气源接口尺寸等的选择以最终确定的供货商设计计算选型为准。"]
[31,null,null,"临界压力 Critical Press Mpa"]
[32,null,null,"噪音 Noise Level",{"$nulls":6},"带符合工艺及仪表要求的配对法兰，垫片(RPTFE)、紧固件及其它阀内安装附件。"]
[33,null,null,"气源故障阀开/关/保持FC/FO/FL",{"$nulls":3},"FC"]
[34,"阀体/阀芯规格 ",null,"型号 Model"]
[35,"Body/Plug ",null,"阀形式 Valve Style",{"$nulls":3},"球阀"]
[36,"Specification",null,"流开/流关 Flow Open/Close"]
[37,null,null,"阀座数量 Seat NO."]
[38,null,null,"阀芯形式 Plug Type",{"$nulls":3},"浮动O型球"]
[39,null,null,"阀口径 Port size",{"$nulls":3},{"$f":"H980","v":"DN100"}]
[40,null,null,"流量特性 Flow Characteristic",{"$nulls":3},"ON-OFF"]
[41,null,null,"阀体材质 Body Material",{"$nulls":3},"CF8"]
[42,null,null,"阀芯材质 Plug Material",{"$nulls":3},304]
[43,null,null,"阀座材质 Seat Material",{"$nulls":3},304]
[44,null,null,"阀杆材质 Stem Material",{"$nulls":3},630]
[45,null,null,"连接尺寸","尺寸  Size",null,null,{"$f":"H993","v":"DN100"}]
[46,null,null,"Process","标准 Rating",null,null,"HG20592-2009(B) PN16 SO-RF"]
[47,null,null,"connection"]
[48,null,null,"法兰材质 Flange Material",{"$nulls":3},"同阀体"]
[49,null,null,"填料 Packing",{"$nulls":3},"PTFE"]
[50,null,null,"泄漏等级 Leakage Class",{"$nulls":3},"ANSI V"]
[1,"位号 TAG NO.",{"$nulls":5},"1KV-3008",null,null,"阀盖形式 Bonnet Type",{"$nulls":3},"供应商填写"]
[2,{"$nulls":9},"允许最大压差 Allow △P Mpa(G)",{"$nulls":3},"供应商填写"]
[3,"数量 Q'ty",{"$nulls":5},1,null,null,"最大开度 Open %AT MAX.Flow",{"$nulls":3},"供应商填写"]
[4,"用途   Service",{"$nulls":5},"1V3502半成品高位槽进料开关阀",null,null,"计算CV  CALC.Cv",{"$nulls":3},"供应商填写"]
[5,{"$nulls":9},"选择CV Selected Cv",{"$nulls":3},"供应商填写"]
[6,"P&ID号 P&ID NO",{"$nulls":5},"20241215-03-GY-03- 01",null,null,"连接形式 Connection Type",{"$nulls":3},"法兰式"]
[7]
[8,"管道或设备号 LINE ＆ EQUIP.NO.",{"$nulls":5},"1PLS-3503-100-C2S-N",null,null,"执行机构 Actuator"]
[9,{"$nulls":9},"型号 Model"]
[10,"流体参数",null,"介质 ",{"$nulls":3},"工艺固液混合物(PPS+水 )",null,null,"型式 Type",{"$nulls":3},"单作用活塞式"]
[11,"Fluid data",null,"Fluid",{"$nulls":6},"作用形式 Action Style",{"$nulls":3},"气开"]
[12,null,null,"压力","阀前压力",null,null,0.04,null,null,"弹簧范围 Spring Range"]
[13,null,null,"Press","Upstream Pressure",{"$nulls":5},"行程 Travel"]
[14,{"$nulls":3},"阀后压力",null,null,0.02,null,null,"手轮 Hand Wheel",{"$nulls":3},"YES"]
[15,{"$nulls":3},"Downstream Pressure",{"$nulls":5},"供气压力 Air Supply Press",{"$nulls":3},"400~700kpa"]
[16,{"$nulls":3},"阀关闭压差",null,null,0.04,null,null,"气信号接口尺寸 PNEU.CONN.Size",{"$nulls":3},"1/4\"NPT"]
[17,{"$nulls":3},"Shut-off Diff Pressure"]
[18,{"$nulls":3},"单位 Unit",null,null,"Mpa(G)",null,null,"附件 Accessories"]
[19,null,null,"温度 Temp.","操作Oper.",null,null,30,null,null,"过滤减压阀 Regulator ",{"$nulls":3},"YES"]
[20,null,null,"  (Deg. C)","设计Des.",{"$nulls":5},"限位开关 Limited Switch ",{"$nulls":3},"YES"]
[21,null,null,"密度 Density","操作Oper.",null,null,"1040kg/m3",null,null,"电磁阀 Solenoid valve",{"$nulls":3},"二位三通，低功耗"]
[22,null,null,"流量","最小 Min.",{"$nulls":5},"电源 Power Supply",{"$nulls":3},"24VDC"]
[23,null,null,"Flow rate","正常 Nor.",null,null,30,null,null,"防爆等级 Ex.Certification",{"$nulls":3},"ExdIIBT4"]
[24,{"$nulls":3},"最大 Max.",{"$nulls":5},"电气接口尺寸 ELEC.CONN.Size",{"$nulls":3},"1/2\"NPT(F)"]
[25,{"$nulls":3},"单位 Unit",null,null,"m3/h",null,null,"保位阀 Locked Valve"]
[26,null,null,"管道规格 Specification",{"$nulls":3},"DN100",null,null,"备用钢瓶 Spare Cylinder"]
[27,null,null,"管道材料 Material",{"$nulls":3},"S30408",null,null,"制造厂 Manufacturer"]
[28,null,null,"动力粘度 Viscosity  (CP)",{"$nulls":3},1.53]
[29,null,null,"压缩系数 Compress Factor",{"$nulls":6},"备注 Remarks"]
[30,null,null,"气化压力 Vapor Pressure Mpa",{"$nulls":6},"阀门口径、内件、气源接口尺寸等的选择以最终确定的供货商设计计算选型为准。"]
[31,null,null,"临界压力 Critical Press Mpa"]
[32,null,null,"噪音 Noise Level",{"$nulls":6},"带符合工艺及仪表要求的配对法兰，垫片(RPTFE)、紧固件及其它阀内安装附件。"]
[33,null,null,"气源故障阀开/关/保持FC/FO/FL",{"$nulls":3},"FC"]
[34,"阀体/阀芯规格 ",null,"型号 Model"]
[35,"Body/Plug ",null,"阀形式 Valve Style",{"$nulls":3},"球阀"]
[36,"Specification",null,"流开/流关 Flow Open/Close"]
[37,null,null,"阀座数量 Seat NO."]
[38,null,null,"阀芯形式 Plug Type",{"$nulls":3},"浮动O型球"]
[39,null,null,"阀口径 Port size",{"$nulls":3},{"$f":"H1030","v":"DN100"}]
[40,null,null,"流量特性 Flow Characteristic",{"$nulls":3},"ON-OFF"]
[41,null,null,"阀体材质 Body Material",{"$nulls":3},"CF8"]
[42,null,null,"阀芯材质 Plug Material",{"$nulls":3},304]
[43,null,null,"阀座材质 Seat Material",{"$nulls":3},304]
[44,null,null,"阀杆材质 Stem Material",{"$nulls":3},630]
[45,null,null,"连接尺寸","尺寸  Size",null,null,{"$f":"H1043","v":"DN100"}]
[46,null,null,"Process","标准 Rating",null,null,"HG20592-2009(B) PN16 SO-RF"]
[47,null,null,"connection"]
[48,null,null,"法兰材质 Flange Material",{"$nulls":3},"同阀体"]
[49,null,null,"填料 Packing",{"$nulls":3},"PTFE"]
[50,null,null,"泄漏等级 Leakage Class",{"$nulls":3},"ANSI V"]
[1,"位号 TAG NO.",{"$nulls":5},"1KV-3009",null,null,"阀盖形式 Bonnet Type",{"$nulls":3},"供应商填写"]
[2,{"$nulls":9},"允许最大压差 Allow △P Mpa(G)",{"$nulls":3},"供应商填写"]
[3,"数量 Q'ty",{"$nulls":5},1,null,null,"最大开度 Open %AT MAX.Flow",{"$nulls":3},"供应商填写"]
[4,"用途   Service",{"$nulls":5},"1V3001B混料罐氮气反吹开关阀",null,null,"计算CV  CALC.Cv",{"$nulls":3},"供应商填写"]
[5,{"$nulls":9},"选择CV Selected Cv",{"$nulls":3},"供应商填写"]
[6,"P&ID号 P&ID NO",{"$nulls":5},"20241215-03-GY-03- 01",null,null,"连接形式 Connection Type",{"$nulls":3},"法兰式"]
[7]
[8,"管道或设备号 LINE ＆ EQUIP.NO.",{"$nulls":5},"1N1-3002-25-C2S-N",null,null,"执行机构 Actuator"]
[9,{"$nulls":9},"型号 Model"]
[10,"流体参数",null,"介质 ",{"$nulls":3},"氮气",null,null,"型式 Type",{"$nulls":3},"单作用活塞式"]
[11,"Fluid data",null,"Fluid",{"$nulls":6},"作用形式 Action Style",{"$nulls":3},"气开"]
[12,null,null,"压力","阀前压力",null,null,0.4,null,null,"弹簧范围 Spring Range"]
[13,null,null,"Press","Upstream Pressure",{"$nulls":5},"行程 Travel"]
[14,{"$nulls":3},"阀后压力",null,null,0.36,null,null,"手轮 Hand Wheel",{"$nulls":3},"YES"]
[15,{"$nulls":3},"Downstream Pressure",{"$nulls":5},"供气压力 Air Supply Press",{"$nulls":3},"400~700kpa"]
[16,{"$nulls":3},"阀关闭压差",null,null,0.4,null,null,"气信号接口尺寸 PNEU.CONN.Size",{"$nulls":3},"1/4\"NPT"]
[17,{"$nulls":3},"Shut-off Diff Pressure"]
[18,{"$nulls":3},"单位 Unit",null,null,"Mpa(G)",null,null,"附件 Accessories"]
[19,null,null,"温度 Temp.","操作Oper.",null,null,"常温",null,null,"过滤减压阀 Regulator ",{"$nulls":3},"YES"]
[20,null,null,"  (Deg. C)","设计Des.",{"$nulls":5},"限位开关 Limited Switch ",{"$nulls":3},"YES"]
[21,null,null,"密度 Density","操作Oper.",null,null,"1.24kg/m3（标）",null,null,"电磁阀 Solenoid valve",{"$nulls":3},"二位三通，低功耗"]
[22,null,null,"流量","最小 Min.",{"$nulls":5},"电源 Power Supply",{"$nulls":3},"24VDC"]
[23,null,null,"Flow rate","正常 Nor.",null,null,15,null,null,"防爆等级 Ex.Certification",{"$nulls":3},"ExdIIBT4"]
[24,{"$nulls":3},"最大 Max.",{"$nulls":5},"电气接口尺寸 ELEC.CONN.Size",{"$nulls":3},"1/2\"NPT(F)"]
[25,{"$nulls":3},"单位 Unit",null,null,"m3/h",null,null,"保位阀 Locked Valve"]
[26,null,null,"管道规格 Specification",{"$nulls":3},"DN25",null,null,"备用钢瓶 Spare Cylinder"]
[27,null,null,"管道材料 Material",{"$nulls":3},"S30408",null,null,"制造厂 Manufacturer"]
[28,null,null,"动力粘度 Viscosity  (CP)"]
[29,null,null,"压缩系数 Compress Factor",{"$nulls":6},"备注 Remarks"]
[30,null,null,"气化压力 Vapor Pressure Mpa",{"$nulls":6},"阀门口径、内件、气源接口尺寸等的选择以最终确定的供货商设计计算选型为准。"]
[31,null,null,"临界压力 Critical Press Mpa"]
[32,null,null,"噪音 Noise Level",{"$nulls":6},"带符合工艺及仪表要求的配对法兰，垫片(RPTFE)、紧固件及其它阀内安装附件。"]
[33,null,null,"气源故障阀开/关/保持FC/FO/FL",{"$nulls":3},"FC"]
[34,"阀体/阀芯规格 ",null,"型号 Model"]
[35,"Body/Plug ",null,"阀形式 Valve Style",{"$nulls":3},"球阀"]
[36,"Specification",null,"流开/流关 Flow Open/Close"]
[37,null,null,"阀座数量 Seat NO."]
[38,null,null,"阀芯形式 Plug Type",{"$nulls":3},"浮动O型球"]
[39,null,null,"阀口径 Port size",{"$nulls":3},{"$f":"H1080","v":"DN25"}]
[40,null,null,"流量特性 Flow Characteristic",{"$nulls":3},"ON-OFF"]
[41,null,null,"阀体材质 Body Material",{"$nulls":3},"CF8"]
[42,null,null,"阀芯材质 Plug Material",{"$nulls":3},304]
[43,null,null,"阀座材质 Seat Material",{"$nulls":3},304]
[44,null,null,"阀杆材质 Stem Material",{"$nulls":3},630]
[45,null,null,"连接尺寸","尺寸  Size",null,null,{"$f":"H1093","v":"DN25"}]
[46,null,null,"Process","标准 Rating",null,null,"HG20592-2009(B) PN16 SO-RF"]
[47,null,null,"connection"]
[48,null,null,"法兰材质 Flange Material",{"$nulls":3},"同阀体"]
[49,null,null,"填料 Packing",{"$nulls":3},"PTFE"]
[50,null,null,"泄漏等级 Leakage Class",{"$nulls":3},"ANSI V"]
[1,"位号 TAG NO.",{"$nulls":5},"1KV-3（101B-401B)",null,null,"阀盖形式 Bonnet Type",{"$nulls":3},"供应商填写"]
[2,{"$nulls":9},"允许最大压差 Allow △P Mpa(G)",{"$nulls":3},"供应商填写"]
[3,"数量 Q'ty",{"$nulls":5},4,null,null,"最大开度 Open %AT MAX.Flow",{"$nulls":3},"供应商填写"]
[4,"用途   Service",{"$nulls":5},"1M3(101-401)半成品离心机进料开关阀",null,null,"计算CV  CALC.Cv",{"$nulls":3},"供应商填写"]
[5,{"$nulls":9},"选择CV Selected Cv",{"$nulls":3},"供应商填写"]
[6,"P&ID号 P&ID NO",{"$nulls":5},"20241215-03-GY-03- 02A",null,null,"连接形式 Connection Type",{"$nulls":3},"法兰式"]
[7]
[8,"管道或设备号 LINE ＆ EQUIP.NO.",{"$nulls":5},"1PLS-3101-100-C2S-N",null,null,"执行机构 Actuator"]
[9,{"$nulls":9},"型号 Model"]
[10,"流体参数",null,"介质 ",{"$nulls":3},"工艺固液混合物(PPS+水 )",null,null,"型式 Type",{"$nulls":3},"单作用活塞式"]
[11,"Fluid data",null,"Fluid",{"$nulls":6},"作用形式 Action Style",{"$nulls":3},"气开"]
[12,null,null,"压力","阀前压力",null,null,0.04,null,null,"弹簧范围 Spring Range"]
[13,null,null,"Press","Upstream Pressure",{"$nulls":5},"行程 Travel"]
[14,{"$nulls":3},"阀后压力",null,null,0.02,null,null,"手轮 Hand Wheel",{"$nulls":3},"YES"]
[15,{"$nulls":3},"Downstream Pressure",{"$nulls":5},"供气压力 Air Supply Press",{"$nulls":3},"400~700kpa"]
[16,{"$nulls":3},"阀关闭压差",null,null,0.04,null,null,"气信号接口尺寸 PNEU.CONN.Size",{"$nulls":3},"1/4\"NPT"]
[17,{"$nulls":3},"Shut-off Diff Pressure"]
[18,{"$nulls":3},"单位 Unit",null,null,"Mpa(G)",null,null,"附件 Accessories"]
[19,null,null,"温度 Temp.","操作Oper.",null,null,30,null,null,"过滤减压阀 Regulator ",{"$nulls":3},"YES"]
[20,null,null,"  (Deg. C)","设计Des.",{"$nulls":5},"限位开关 Limited Switch ",{"$nulls":3},"YES"]
[21,null,null,"密度 Density","操作Oper.",null,null,"1040kg/m3",null,null,"电磁阀 Solenoid valve",{"$nulls":3},"二位三通，低功耗"]
[22,null,null,"流量","最小 Min.",{"$nulls":5},"电源 Power Supply",{"$nulls":3},"24VDC"]
[23,null,null,"Flow rate","正常 Nor.",null,null,30,null,null,"防爆等级 Ex.Certification",{"$nulls":3},"ExdIIBT4"]
[24,{"$nulls":3},"最大 Max.",{"$nulls":5},"电气接口尺寸 ELEC.CONN.Size",{"$nulls":3},"1/2\"NPT(F)"]
[25,{"$nulls":3},"单位 Unit",null,null,"m3/h",null,null,"保位阀 Locked Valve"]
[26,null,null,"管道规格 Specification",{"$nulls":3},"DN100",null,null,"备用钢瓶 Spare Cylinder"]
[27,null,null,"管道材料 Material",{"$nulls":3},"S30408",null,null,"制造厂 Manufacturer"]
[28,null,null,"动力粘度 Viscosity  (CP)",{"$nulls":3},1.53]
[29,null,null,"压缩系数 Compress Factor",{"$nulls":6},"备注 Remarks"]
[30,null,null,"气化压力 Vapor Pressure Mpa",{"$nulls":6},"阀门口径、内件、气源接口尺寸等的选择以最终确定的供货商设计计算选型为准。"]
[31,null,null,"临界压力 Critical Press Mpa"]
[32,null,null,"噪音 Noise Level",{"$nulls":6},"带符合工艺及仪表要求的配对法兰，垫片(RPTFE)、紧固件及其它阀内安装附件。"]
[33,null,null,"气源故障阀开/关/保持FC/FO/FL",{"$nulls":3},"FC"]
[34,"阀体/阀芯规格 ",null,"型号 Model"]
[35,"Body/Plug ",null,"阀形式 Valve Style",{"$nulls":3},"球阀"]
[36,"Specification",null,"流开/流关 Flow Open/Close"]
[37,null,null,"阀座数量 Seat NO."]
[38,null,null,"阀芯形式 Plug Type",{"$nulls":3},"浮动O型球"]
[39,null,null,"阀口径 Port size",{"$nulls":3},{"$f":"H1130","v":"DN100"}]
[40,null,null,"流量特性 Flow Characteristic",{"$nulls":3},"ON-OFF"]
[41,null,null,"阀体材质 Body Material",{"$nulls":3},"CF8"]
[42,null,null,"阀芯材质 Plug Material",{"$nulls":3},304]
[43,null,null,"阀座材质 Seat Material",{"$nulls":3},304]
[44,null,null,"阀杆材质 Stem Material",{"$nulls":3},630]
[45,null,null,"连接尺寸","尺寸  Size",null,null,{"$f":"H1143","v":"DN100"}]
[46,null,null,"Process","标准 Rating",null,null,"HG20592-2009(B) PN16 SO-RF"]
[47,null,null,"connection"]
[48,null,null,"法兰材质 Flange Material",{"$nulls":3},"同阀体"]
[49,null,null,"填料 Packing",{"$nulls":3},"PTFE"]
[50,null,null,"泄漏等级 Leakage Class",{"$nulls":3},"ANSI V"]
[1,"位号 TAG NO.",{"$nulls":5},"1KV-3512",null,null,"阀盖形式 Bonnet Type",{"$nulls":3},"供应商填写"]
[2,{"$nulls":9},"允许最大压差 Allow △P Mpa(G)",{"$nulls":3},"供应商填写"]
[3,"数量 Q'ty",{"$nulls":5},1,null,null,"最大开度 Open %AT MAX.Flow",{"$nulls":3},"供应商填写"]
[4,"用途   Service",{"$nulls":5},"1M3010二合一过滤干燥机出料开关阀",null,null,"计算CV  CALC.Cv",{"$nulls":3},"供应商填写"]
[5,{"$nulls":9},"选择CV Selected Cv",{"$nulls":3},"供应商填写"]
[6,"P&ID号 P&ID NO",{"$nulls":5},"20241215-03-GY-03- 02E",null,null,"连接形式 Connection Type",{"$nulls":3},"法兰式"]
[7]
[8,"管道或设备号 LINE ＆ EQUIP.NO.",{"$nulls":5},"1PL-3024-100-C2S-N",null,null,"执行机构 Actuator"]
[9,{"$nulls":9},"型号 Model"]
[10,"流体参数",null,"介质 ",{"$nulls":3},"工艺固液混合物( PPS+水+醋酸)",null,null,"型式 Type",{"$nulls":3},"单作用活塞式"]
[11,"Fluid data",null,"Fluid",{"$nulls":6},"作用形式 Action Style",{"$nulls":3},"气开"]
[12,null,null,"压力","阀前压力",null,null,0.02,null,null,"弹簧范围 Spring Range"]
[13,null,null,"Press","Upstream Pressure",{"$nulls":5},"行程 Travel"]
[14,{"$nulls":3},"阀后压力",null,null,0.01,null,null,"手轮 Hand Wheel",{"$nulls":3},"YES"]
[15,{"$nulls":3},"Downstream Pressure",{"$nulls":5},"供气压力 Air Supply Press",{"$nulls":3},"400~700kpa"]
[16,{"$nulls":3},"阀关闭压差",null,null,0.02,null,null,"气信号接口尺寸 PNEU.CONN.Size",{"$nulls":3},"1/4\"NPT"]
[17,{"$nulls":3},"Shut-off Diff Pressure"]
[18,{"$nulls":3},"单位 Unit",null,null,"Mpa(G)",null,null,"附件 Accessories"]
[19,null,null,"温度 Temp.","操作Oper.",null,null,50,null,null,"过滤减压阀 Regulator ",{"$nulls":3},"YES"]
[20,null,null,"  (Deg. C)","设计Des.",{"$nulls":5},"限位开关 Limited Switch ",{"$nulls":3},"YES"]
[21,null,null,"密度 Density","操作Oper.",null,null,"1040kg/m3",null,null,"电磁阀 Solenoid valve",{"$nulls":3},"二位三通，低功耗"]
[22,null,null,"流量","最小 Min.",{"$nulls":5},"电源 Power Supply",{"$nulls":3},"24VDC"]
[23,null,null,"Flow rate","正常 Nor.",null,null,30,null,null,"防爆等级 Ex.Certification",{"$nulls":3},"ExdIIBT4"]
[24,{"$nulls":3},"最大 Max.",{"$nulls":5},"电气接口尺寸 ELEC.CONN.Size",{"$nulls":3},"1/2\"NPT(F)"]
[25,{"$nulls":3},"单位 Unit",null,null,"m3/h",null,null,"保位阀 Locked Valve"]
[26,null,null,"管道规格 Specification",{"$nulls":3},"DN100",null,null,"备用钢瓶 Spare Cylinder"]
[27,null,null,"管道材料 Material",{"$nulls":3},"316L",null,null,"制造厂 Manufacturer"]
[28,null,null,"动力粘度 Viscosity  (CP)",{"$nulls":3},1.53]
[29,null,null,"压缩系数 Compress Factor",{"$nulls":6},"备注 Remarks"]
[30,null,null,"气化压力 Vapor Pressure Mpa",{"$nulls":6},"阀门口径、内件、气源接口尺寸等的选择以最终确定的供货商设计计算选型为准。"]
[31,null,null,"临界压力 Critical Press Mpa"]
[32,null,null,"噪音 Noise Level",{"$nulls":6},"带符合工艺及仪表要求的配对法兰，垫片(RPTFE)、紧固件及其它阀内安装附件。"]
[33,null,null,"气源故障阀开/关/保持FC/FO/FL",{"$nulls":3},"FC"]
[34,"阀体/阀芯规格 ",null,"型号 Model"]
[35,"Body/Plug ",null,"阀形式 Valve Style",{"$nulls":3},"球阀"]
[36,"Specification",null,"流开/流关 Flow Open/Close"]
[37,null,null,"阀座数量 Seat NO."]
[38,null,null,"阀芯形式 Plug Type",{"$nulls":3},"浮动O型球"]
[39,null,null,"阀口径 Port size",{"$nulls":3},{"$f":"H1180","v":"DN100"}]
[40,null,null,"流量特性 Flow Characteristic",{"$nulls":3},"ON-OFF"]
[41,null,null,"阀体材质 Body Material",{"$nulls":3},"CF3M"]
[42,null,null,"阀芯材质 Plug Material",{"$nulls":3},"316L"]
[43,null,null,"阀座材质 Seat Material",{"$nulls":3},"316L"]
[44,null,null,"阀杆材质 Stem Material",{"$nulls":3},"S20910"]
[45,null,null,"连接尺寸","尺寸  Size",null,null,{"$f":"H1193","v":"DN100"}]
[46,null,null,"Process","标准 Rating",null,null,"HG20592-2009(B) PN16 SO-RF"]
[47,null,null,"connection"]
[48,null,null,"法兰材质 Flange Material",{"$nulls":3},"同阀体"]
[49,null,null,"填料 Packing",{"$nulls":3},"PTFE"]
[50,null,null,"泄漏等级 Leakage Class",{"$nulls":3},"ANSI V"]
[1,"位号 TAG NO.",{"$nulls":5},"1FV-5001C",null,null,"阀盖形式 Bonnet Type",{"$nulls":3},"供应商填写"]
[2,{"$nulls":9},"允许最大压差 Allow △P Mpa(G)",{"$nulls":3},"供应商填写"]
[3,"数量 Q'ty",{"$nulls":5},1,null,null,"最大开度 Open %AT MAX.Flow",{"$nulls":3},"供应商填写"]
[4,"用途   Service",{"$nulls":5},"1V5303搅拌罐补水流量开关阀",null,null,"计算CV  CALC.Cv",{"$nulls":3},"供应商填写"]
[5,{"$nulls":9},"选择CV Selected Cv",{"$nulls":3},"供应商填写"]
[6,"P&ID号 P&ID NO",{"$nulls":5},"20241215-05-GY-03- 04",null,null,"连接形式 Connection Type",{"$nulls":3},"法兰式"]
[7]
[8,"管道或设备号 LINE ＆ EQUIP.NO.",{"$nulls":5},"1PW-5003-50-C2S-H",null,null,"执行机构 Actuator"]
[9,{"$nulls":9},"型号 Model"]
[10,"流体参数",null,"介质 ",{"$nulls":3},"冷凝液（生蒸汽冷凝液）",null,null,"型式 Type",{"$nulls":3},"单作用活塞式"]
[11,"Fluid data",null,"Fluid",{"$nulls":6},"作用形式 Action Style",{"$nulls":3},"气开"]
[12,null,null,"压力","阀前压力",null,null,0.4,null,null,"弹簧范围 Spring Range"]
[13,null,null,"Press","Upstream Pressure",{"$nulls":5},"行程 Travel"]
[14,{"$nulls":3},"阀后压力",null,null,0.36,null,null,"手轮 Hand Wheel",{"$nulls":3},"YES"]
[15,{"$nulls":3},"Downstream Pressure",{"$nulls":5},"供气压力 Air Supply Press",{"$nulls":3},"400~700kpa"]
[16,{"$nulls":3},"阀关闭压差",null,null,0.4,null,null,"气信号接口尺寸 PNEU.CONN.Size",{"$nulls":3},"1/4\"NPT"]
[17,{"$nulls":3},"Shut-off Diff Pressure"]
[18,{"$nulls":3},"单位 Unit",null,null,"Mpa(G)",null,null,"附件 Accessories"]
[19,null,null,"温度 Temp.","操作Oper.",null,null,"常温",null,null,"过滤减压阀 Regulator ",{"$nulls":3},"YES"]
[20,null,null,"  (Deg. C)","设计Des.",{"$nulls":5},"限位开关 Limited Switch ",{"$nulls":3},"YES"]
[21,null,null,"密度 Density","操作Oper.",null,null,"1000kg/m3",null,null,"电磁阀 Solenoid valve",{"$nulls":3},"二位三通，低功耗"]
[22,null,null,"流量","最小 Min.",{"$nulls":5},"电源 Power Supply",{"$nulls":3},"24VDC"]
[23,null,null,"Flow rate","正常 Nor.",null,null,14,null,null,"防爆等级 Ex.Certification",{"$nulls":3},"ExdIIBT4"]
[24,{"$nulls":3},"最大 Max.",{"$nulls":5},"电气接口尺寸 ELEC.CONN.Size",{"$nulls":3},"1/2\"NPT(F)"]
[25,{"$nulls":3},"单位 Unit",null,null,"m3/h",null,null,"保位阀 Locked Valve"]
[26,null,null,"管道规格 Specification",{"$nulls":3},"DN50",null,null,"备用钢瓶 Spare Cylinder"]
[27,null,null,"管道材料 Material",{"$nulls":3},"S30408",null,null,"制造厂 Manufacturer"]
[28,null,null,"动力粘度 Viscosity  (CP)",{"$nulls":3},0.84]
[29,null,null,"压缩系数 Compress Factor",{"$nulls":6},"备注 Remarks"]
[30,null,null,"气化压力 Vapor Pressure Mpa",{"$nulls":6},"阀门口径、内件、气源接口尺寸等的选择以最终确定的供货商设计计算选型为准。"]
[31,null,null,"临界压力 Critical Press Mpa"]
[32,null,null,"噪音 Noise Level",{"$nulls":6},"带符合工艺及仪表要求的配对法兰，垫片(RPTFE)、紧固件及其它阀内安装附件。"]
[33,null,null,"气源故障阀开/关/保持FC/FO/FL",{"$nulls":3},"FC"]
[34,"阀体/阀芯规格 ",null,"型号 Model"]
[35,"Body/Plug ",null,"阀形式 Valve Style",{"$nulls":3},"球阀"]
[36,"Specification",null,"流开/流关 Flow Open/Close"]
[37,null,null,"阀座数量 Seat NO."]
[38,null,null,"阀芯形式 Plug Type",{"$nulls":3},"浮动O型球"]
[39,null,null,"阀口径 Port size",{"$nulls":3},{"$f":"H1230","v":"DN50"}]
[40,null,null,"流量特性 Flow Characteristic",{"$nulls":3},"ON-OFF"]
[41,null,null,"阀体材质 Body Material",{"$nulls":3},"CF8"]
[42,null,null,"阀芯材质 Plug Material",{"$nulls":3},304]
[43,null,null,"阀座材质 Seat Material",{"$nulls":3},304]
[44,null,null,"阀杆材质 Stem Material",{"$nulls":3},630]
[45,null,null,"连接尺寸","尺寸  Size",null,null,{"$f":"H1243","v":"DN50"}]
[46,null,null,"Process","标准 Rating",null,null,"HG20592-2009(B) PN16 SO-RF"]
[47,null,null,"connection"]
[48,null,null,"法兰材质 Flange Material",{"$nulls":3},"同阀体"]
[49,null,null,"填料 Packing",{"$nulls":3},"PTFE"]
[50,null,null,"泄漏等级 Leakage Class",{"$nulls":3},"ANSI V"]